BANGLADESH POWER DEVELOPMENT BOARD

BIDDING DOCUMENT

For

Electrification at Bhashanchar of Noakhali District

(Single Stage Two Envelope Bidding Process)

Bidding Document

(Volume 3 of 3 of the Bidding Document)

Invitation for Tender No: 27.11.0000.101.14.079.25-2337,  Dated: 14/09/2025

Secretary

Bangladesh Power Development Board

Wapda Building (1st Floor), Motijheel, C/A.

Dhaka, Bangladesh

SEPTEMBER, 2025

Guaranteed Technical Particulars (GTP)

of

Electrification at Bhashanchar of Noakhali District Project

The following GTP to be filled up appropriately, then Seal & Signed by both manufacturer and bidder on Manufacturer’s Letterhead Pad. Otherwise his bid shall be non-responsive.

Table of Contents

- Technical Guarantee Parameters of the Entire system

- Guaranteed Technical Particulars (GTP) of Solar Photovoltaic Module

- Guaranteed Technical Particulars (GTP) of Grid Tied Inverter

- Guaranteed Technical Particulars (GTP) of PCS/Battery Inverter

- Guaranteed Technical Particulars (GTP) of  Battery Energy Storage System (BESS)

- Guaranteed Technical Particulars (GTP) of  Power Transformer

- Guaranteed Technical Particulars (GTP) of  Energy meter (11kV CT/PT Meter)

- Guaranteed Technical Particulars (GTP) of  Pyranometer and Data Logger

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 250kVA Distribution Transformer

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 100kVA Distribution Transformer

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 50kVA Distribution Transformer

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 10kVA Distribution Transformer

- Guaranteed Technical Particulars (GTP) of Switchgear, Control & Protection Panel

- Guaranteed Technical Particulars (GTP) of PCMS Server

- Guaranteed Technical Particulars (GTP) of PCMS Software

- Guaranteed Techncial Particulars ( GTP) for EMS

- Guaranteed Technical Particulars (GTP) of Battery Charger

- Guaranteed Technical Particulars (GTP) of UPS/Battery

- Guaranteed Technical Particulars for 12M, 450daN Galvanized Telescopic Steel Pole

- Guaranteed Technical Particulars for 12M, 350daN Galvanized Telescopic Steel Pole

- Guaranteed Technical Particulars for 9M, 300daN Galvanized Telescopic Steel Pole

- Guaranteed Technical Particulars for 9M, 200daN Galvanized Telescopic Steel Pole

- Guaranteed Technical Particulars for ACSR DOG Conductor

- Guaranteed Technical Particulars for AAC WASP (Insulated) Conductor

- Guaranteed Technical Particulars for AAC ANT (Insulated) Conductor

- Guaranteed Technical Particulars (GTP) for Platform Structure for Distribution Transformer

- Guaranteed Technical Particulars (GTP) of  Disel Generator

- Guaranteed Technical Particulars (GTP) Double Cabin Disel Pick Up

- Guaranteed Technical Particulars (GTP) of Electric Vehicle

- Guaranteed Technical Particulars for Single-Core, 35 mm2 PVC Insulated and PVC Sheathed Copper Cable

- Guaranteed Technical Particulars for Single-Core, 25 mm2 PVC Insulated and PVC Sheathed Copper Cable

- Guaranteed Technical Particulars for PVC Insulated Quadruplex Copper Cable (4⨯16rm)

- Guaranteed Technical Particulars For Pvc Insulated Quadruplex Copper Cable (4⨯6rm)

- Guaranteed Technical Particulars For Pvc Insulated Duplex Copper Cable (4rm)

- Guaranteed Technical Particulars Of 11kv, Xlpe, 3c X 70mm2 Copper Cable

- Manufacturer’s Guaranteed Technical Data Schedule For Of 230 Volt, 10(60) A, Single Phase Digital Energy Meter

- Manufacturer’s Guaranteed Technical Data Schedule For 110v, 3x5(6)A, 3-Phase, 4-Wire Accuracy Class 0.2s Solid State Double Tariff Programmable Energy Meter.

- Manufacturer’s Guaranteed Technical Data Schedule For 400v,  3x10(60) A, 3-Phase, 4-Wire Solid State Double Tariff Fully Programmable Energy Meter

key:

probably unnecessary to specifiy likely covered by system performance

attention

- Technical Guarantee Parameters of the Entire system

- Technical Guarantee Pqrameters of the PV System

Subject to compliance with the foregoing preconditions, the Contractor guarantees as follows:

| Technical Guarantee | Minimum (or Maximum, as appropriate) Requirement |
| --- | --- |
| A. PV Plant (during Commissioning and Operational Acceptance) | - PV plant to meet the minimum nominal installed DC Capacity [10MWp] - PV Plant to meet minimum installed AC capacity [8 MWac] measured on 11kV busbar. - The Bidder shall ensure that the proposed PV Plant achieves a minimum Performance Ratio (PR) of 80% at the time of commissioning. The methodology for PR calculation is detailed in Appendix 9. If the Contractor fails to achieve the guaranteed performance levels, the Contractor shall at its own cost rectify all the defects identified during the test and take necessary steps/efforts to pass the test within the stipulated time span. Subsequent to rectification the production shall be re-tested, if the values are again below the guaranteed performance levels. |
| B. At Final Acceptance Certificate | - The DC capacity of the PV Plant for the purpose of Performance Ratio (PR) calculation shall take into account the degradation of the PV modules. The degradation rate shall be considered in accordance with the values specified in the Guaranteed Technical Particulars (GTP) of the PV modules provided by the Contractor. - The Contractor shall maintain a monthly Performance Ratio (PR) of at least 80% during the first two (2) years of operation. N.B: Failure to achieve the guaranteed PR shall trigger remedies but not limited to, the Contractor being required, at its own cost and expense, to make such changes, modifications, and/or additions to the Facilities or any part thereof that are necessary to attain the guaranteed PR, and to request the Employer to repeat the Guarantee Test. |

- Technical Guarantee parameters of the Battery Energy Storage System (BESS)

| Technical Guarantee | Minimum Requirement |
| --- | --- |
| C. BESS (during Commissioning and Operational Acceptance) | - Available Energy capacity [16MWh] discharged/charged (on high tension side of 11 kV step up transformer) - Nominal [5MW] and Max Reactive Power [5 MVAr] Capacity for the life of the installation. - Uptime of [97%] - Round-trip efficiency of [90%] |
| D. for Final Acceptance Certificate (2 years after Operational Acceptance) | - Available Energy capacity [] discharged/charged (on high tension side of 11 kV step up transformer considering BESS capacity degradation factor. - Capacity degradation of less than [3.5% p.a], from Energy Capacity measured at Operational Acceptance - Nominal [5MW] and Max Reactive Power [5 MVAr] Capacity for the life of the installation. - Uptime of [97%] - Round-trip efficiency of []; considering degradation factor |
| If the Contractor fails to achieve the Technical Guarantee ,the Contractor shall at its own cost rectify all the defects identified during the test and take necessary steps/efforts to pass the test within the stipulated time span |  |

**The value given within the square bracket [  ] is indicative for each guarantee parameter mentioned in the above table. If the Contractor fails to meet the full Technical Guarantee but achieves the minimum levels, it shall modify or upgrade the Facilities at its own cost.

- Guaranteed Technical Particulars (GTP) of Solar Photovoltaic Module

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Description of the Item | Solar PV Module |  |
| 2 | Name of the Manufacturer | To be mentioned |  |
| 3 | Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | IEC61215:2021/IEC61730:2023/IEC61701 / IEC62716 / IEC60068/IEC62804/ISO9001:2015/ISO14001:2015/ISO45001:2018 |  |
| 5 | Model number | To be mentioned |  |
| 6 | Type of solar Cells | Mono Crystalline/mono crystalline bifacial |  |
| 7 | Rated Power /Maximum Power (Pmax) | Minimum 650 Wp at STC, (Standard Testing Conditions) |  |
| 8 | Power Tolerance (STC) | 0~+3% |  |
| 9 | Voltage at Pmax (V mp) | To be mentioned |  |
| 10 | Current at Pmax (I mp) | To be mentioned |  |
| 11 | Open circuit voltage (Voc) | To be mentioned |  |
| 12 | Temperature Co-efficient (Pmax) | Maximum -0.29%/ºC or better |  |
| 13 | Temperature Co-efficient (Voc) | Maximum -0.25%/ºC or better |  |
| 14 | Number of cells in series | To be mentioned |  |
| 15 | Module Efficiency | Minimum 22.5% |  |
| 16 | Front Glass | Minimum 2.00 mm, Anti-reflection Coating, High Transmission, Low Iron, Tempered Glass |  |
| 17 | Frame | Anodized Aluminum Alloy |  |
| 18 | Operating Temperature | -40ºC to +85ºC |  |
| 19 | Minimum Static Load front and back (e.g. wind) | Fron 5400Pascal Rear 2400Pascal |  |
| 20 | Junction Box | IP 68 rated |  |
| 21 | Connector | MC4 |  |
| 22 | Cables Cross Section | Min 4.0 mm2 |  |
| 23 | Cable Length | (-) 1200 mm and (+) 1200 mm |  |
| 24 | Expected Life | 25 years |  |
| 25 | Maximum 1st year Degradation | 2.0% |  |
|  | Maximum Annual Degradation over 25 years life of Module | 0.50% |  |
| 26 | Linear Power Warranty | Minimum 25 years |  |
| 27 | Product Warranty | Minimum 12 years |  |
| 28 | Certifications | UL, TUV , ISO or equivalent |  |
| 29 | Weight and Dimension | To be mentioned |  |
| 30 | Catalogue | To be submitted |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of Grid Tied Inverter

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Name of the Item | Grid Tied Inverter |  |
| 2 | Name of the Manufacturer | To be mentioned |  |
| 3 | Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | IEC 62109-1/-2, IEC 62920, IEC 60947-2, EN 50549-2, IEC 61683 |  |
| 5 | Certifications | To be mentioned |  |
| 6 | Model number | To be mentioned |  |
| INPUT |  |  |  |
| 7 | Max Input Voltage | 1500 V |  |
|  | Startup Voltage | To be mentioned |  |
|  | Minimum No of Independent MPP input | Optional |  |
| OUTPUT |  |  |  |
| 8 | Nominal AC Output Power | Minimum 250 kW |  |
|  | Nominal Output Voltage | To be mentioned |  |
|  | AC Frequency, adjustable | 50 ± 5% Hz |  |
|  | AC Grid Connection | 3 phase, 4 wire |  |
| 9 | Idle power | < 6W |  |
| 10 | Total Harmonic Distortion | < 3% |  |
| 11 | Typical efficiency | Minimum 98% |  |
| 12 | Power Factor | 0.8 leading to 0.8 lagging |  |
| 13 | Reverse Current Protection | To be incorporated |  |
| 14 | DC Reverse Polarity Protection | To be incorporated |  |
| 15 | Anti-Islanding Protection | To be incorporated |  |
| 16 | Ground Fault Monitoring | To be incorporated |  |
| 17 | Degree of Protection | IP66 |  |
| 18 | Communication | RS485 |  |
| 19 | Display monitor | LED. WLAN+APP or Bluetooth+APP |  |
| 20 | Topology | Transformerless |  |
| 21 | Weight and Dimension | To be mentioned |  |
| 22 | Warranty | Minimum 5 years |  |
| 23 | Catalogue | To be submitted |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of PCS/Battery Inverter

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
|  | Model Name | To be mentioned |  |
|  | Name of the Manufacturer | To be mentioned |  |
|  | Address of the Manufacturer | To be mentioned |  |
|  | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC, BS, BDS or equivalent international standards. |  |
| DC Input |  |  |  |
|  | Max. DC input voltage | 1500 V |  |
|  | Min. DC input voltage | To be mentioned |  |
| AC Output |  |  |  |
|  | Rated AC output power | Minimum 200 kW |  |
|  | Rated output voltage | To be mentioned |  |
|  | Grid connection type | Three-phase / PE |  |
|  | Nom. grid frequency/grid frequency range | 50 ± 5% Hz |  |
|  | AC current THD | <3% |  |
|  | Max. efficiency | 98.0% |  |
|  | Standby consumption | < 30 W |  |
|  | Cooling System | Air Cooling |  |
|  | User interface and display | LED indicators, Wi-Fi |  |
|  | PCS inverter monitoring | Ethernet /Modbus RS485 |  |
|  | Degree of Protection | IP 66(Outdoor)/IP 54(indoor) |  |
|  | Black start/Grid Forming | Yes |  |
|  | Overvoltage protection | Yes |  |
|  | Grid monitoring | Yes |  |
|  | Dimensions (WxHxD) | To be mentioned |  |
|  | Weight | To be mentioned |  |
|  | Warranty | 5 years |  |
|  | Catalogue | To be submitted |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of  Battery Energy Storage System (BESS)

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Name of the Item | Battery Energy Storage System |  |
| 2 | Name of the Manufacturer | To be mentioned |  |
| 3 | Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC, BS, BDS or equivalent international standards. |  |
| 5 | Certifications | To be mentioned |  |
| 6 | Model number | To be mentioned |  |
| 7 | Battery Chemistry | To be mentioned |  |
| 8 | Proyection & Housing | IP55 & Container Based |  |
| 9 | Rated Unit Capacity | Maximum 2 MWh |  |
| 10 | Cell capacity | Maximum 300 Ah |  |
| 11 | Cell Voltage | To be mentioned |  |
| 12 | Rated Unit voltage | Left to the bidder |  |
| 13 | Charge/Discharge Rate | 0.5C |  |
| 14 | Cooling | Liquid cooling/Air Cooling |  |
| 15 | Ambient (Outside) Temperature Range | -20°C~55°C |  |
| 16 | Relative Humidity Range | 5%~100% |  |
| 17 | Noise | < 75dB |  |
| 18 | Black start/Grid Forming | Yes |  |
| 20 | Certifications of Standards | IEC 62133 (cell), IEC 62619 (ESS). UL 1642 (cell), UL 9540 (ESS), IEEE 1547 2018 (inverter), UL 1741 (inverter) |  |
| 21 | Dimension | To be mentioned |  |
| 22 | Warranty | Min 10 yrs for all part |  |
| 23 | Communication | Modbus TCP/IP |  |
| 24 | PCMS connection | Yes |  |
| 25 | Cell level monitoring | yes |  |
| 26 | Catalogue | To be submitted |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of  Power Transformer

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Description of the Item | Multi-winding Step Up Transformer |  |
| 2 | Manufacturer’s Name | To be mentioned |  |
| 3 | Country of the Origin | To be mentioned |  |
| 4 | Manufacturer’s Type/ Model No. | To be mentioned |  |
| 5 | Installation | Outdoor, Tropical, High Rainfall & Humidity |  |
| 6 | Type | Core |  |
| 7 | Coolant | Mineral oil |  |
| 8 | Method of Cooling | ONAN |  |
| 9 | kVA Rating | Minimum 3400 KVA |  |
| 10 | Number of Phases | 3 |  |
| 11 | Rated frequency, Hz | 50 |  |
| 12 | Rated primary voltage, V | To be mentioned |  |
| 13 | Rated no load sec. Voltage, kV | 11 |  |
| 14 | Vector group | DYn11 |  |
| 15 | Highest system voltage of : |  |  |
|  | a) Primary winding, V | To be mentioned |  |
|  | b) Secondary winding, kV | 12 |  |
| 16 | Basic insulation level, KV | 75 kV Peak (1.2/50 µs) |  |
| 17 | Power frequency withstand voltage, kV |  |  |
|  | a) HT Side | 12 |  |
|  | b) LT Side | To be mentioned |  |
| 18 | No-Load Loss (W) | To be mentioned |  |
| 19 | Full Load Loss (W) | To be mentioned |  |
| 20 | Percentage Impedence | To be mentioned |  |
| 21 | Type of cooling | ONAN |  |
| 22 | Catalogue | To be submitted |  |
| H.T WINDING |  |  |  |
| 1 | Nominal Rated voltage | 11 KV |  |
| 2 | Maximum system voltage | 12 KV |  |
| 3 | Basic insulation level (minimum) | As per IEC Standard |  |
| 4 | Tap Changer | +2x2.5%, 0, -2x2.5% of rated kV & all fully rated capacity. Tap Changer shall be on off load type |  |
| 5 | Inter phase connection | Wye |  |
| 6 | Bushings | Porcelain, outdoors type with arcing horns of standard gap, mounted on top of tank. Quantity-3 Nos. |  |
| 7 | Power frequency withstand voltage for one minute | As per IEC Standard |  |
| L.T WINDING: |  |  |  |
| 1 | Nominal Rated voltage | To be mentioned (in accordance with the inverter output voltage) |  |
| 2 | Highest system voltage | To be mentioned |  |
| 3 | Basic insulation level (minimum) | To be mentioned |  |
| 4 | Bushings | Porcelain, outdoors type with arcing horns of standard gap, mounted on top of tank. Quantity-3 Nos. |  |
| 5 | Power frequency withstand voltage for one minute | To be mentioned |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of  Energy meter (11kV CT/PT Meter)

| Sl. No. | Description |  |  | Purchaser's Requirement | Manufacture’s particulars |
| --- | --- | --- | --- | --- | --- |
| 1 | Reference Standard |  |  | Relevant ANSI / IEC Standard |  |
| 2 | Manufacturer’s name & address |  |  | Shall be mentioned |  |
| 3 | Manufacturer’s type & model |  |  | Shall be mentioned |  |
| 4 | Construction/connection |  |  | 3-Phase 4-wire solidly grounded neutral |  |
| 5 | Installation |  |  | Indoor installation in A socket [for socket type] |  |
| 6 | Number of element |  |  | 3 (Three) |  |
| 7 | Rated Voltage , Volt |  |  | 110V |  |
| 8 | Minimum Biasing Voltage , Volt |  |  | 40V |  |
| 9 | Variation of Frequency, % |  |  | ± 2% |  |
| 10 | Variation of Voltage, % |  |  | + 10, -20% |  |
| 11 | Accuracy class |  |  | 0.2 (point two) |  |
| 12 | Rated Current |  |  |  |  |
|  | i) |  | Nominal Current , A | = 5 |  |
|  | ii) |  | Maximum Current , A | > 6 |  |
| 13 | Resister Type |  |  | LCD Display |  |
| 14 | Number of Digits (Integer with Decimal), Nos. |  |  | 5 with 1 (Programmable) |  |
| 15 | Starting Current , ma |  |  | 0.1% of Nominal Current |  |
| 16 | Losses at Nominal Load , Watt |  |  | Shall be mentioned |  |
| 17 | Meter Constant , Imp./ |  |  | Shall be mentioned |  |
| 18 | Integration Period |  |  | 30 (Thirty) Minutes |  |
|  | Resetting Period |  |  | 1 (one) month |  |
|  | Cumulative MD transfer |  |  | Built in |  |
|  | Cycle Timing Device |  |  | Built in |  |
| 19 | Size of the Digit of Display, E x H in mm |  |  | 4 x 8 |  |
| 20 | No. of Terminal , Nos. |  |  | 10 (Ten) min |  |
| 21 | Type of socket and country of origin |  |  | To be mentioned |  |
| 22 | Battery Service life and shelf Life (minimum), Year |  |  | 10 (ten) & 15 (fifteen) |  |
| 23 | Year of manufacture |  |  | Shall be mentioned |  |
| 24 | List of Recommended spare parts (if any) , any |  |  | Shall be mentioned |  |
| 25 | Warranty , Year |  |  | 3 (three) |  |
| 26 | Meter Service Life (Min), Year |  |  | 15 (fifteen) |  |
| 27 | Weight of meter , Kg |  |  | Shall be mentioned |  |
| 28 | Dimensions , mm x mm x mm |  |  | Shall be mentioned |  |
| 29 | Outlines, Drawings & Leaflets |  |  | Shall be mentioned |  |
| 30 | Performance Curve for Balanced & Unbalanced load |  |  | Shall be mentioned |  |
| 31 | Meter sealing condition |  |  | Hermetically or Ultrasonic welded |  |
| 32 | a) Country of Origin b) Place of Manufacture c) Place of Testing |  |  | Shall be mentioned |  |
| 33 | Memory Storage |  |  | Shall be mentioned by putting Yes/ No. |  |
|  | i) | Equipment Identification Code |  |  |  |
|  | ii) | Security code |  |  |  |
|  | iii) | Access code |  |  |  |
|  | iv) | Number of Power Interruption with Date & Time |  |  |  |
|  | V | Latest Power Failure- Time & Date |  |  |  |
|  | Vi | Event logs |  |  |  |
|  | vii) | Cumulative kWh, kVarh (Q1 + Q4) Reading for previous two months |  |  |  |
|  | viii) Load profile with 30 min interval at least 90 days for: |  |  |  |  |
|  |  | KWh, kVarh (Q1+Q4) |  |  |  |
|  |  | Phase Voltage or Vh |  |  |  |
|  |  | Phase Amps or Ah |  |  |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of  Pyranometer and Data Logger

| SL No | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| Pyranometer |  |  |  |
| 01 | Description of the Item | Pyranometer |  |
| 02 | Name of the Manufacturer | To be mentioned |  |
| 03 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC or equivalent international standards. |  |
| 04 | Model number | To be mentioned |  |
| 05 | Spectral Range | 285 to 2800 nm |  |
| 06 | Sensitivity | 7 to14 µV/W/m2 |  |
| 07 | Response Time | < 5 s |  |
| 08 | Zero Offset A | < 7 W/ m2 |  |
| 09 | Zero Offset B | < 2 W/ m2 |  |
| 10 | Direction Error (up to 80º with 1 Sun irradiance) | < 10 W/ m2 |  |
| 11 | Operating Temperature Range | -40º C to +80º C |  |
| 12 | Temperature Dependence of Sensitivity (-40º C to +80º C ) | < 1% |  |
| 13 | Maximum Solar Irradiance | 4000 W/ m2 |  |
| 14 | Field of View | 180 º |  |
| Data Logger |  |  |  |
| 01 | Description of the Item | Data Logger |  |
| 02 | Name of the Manufacturer | To be mentined |  |
| 03 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC or equivalent international standards. |  |
| 04 | Model number | To be mentioned |  |
| 05 | Local Communication | USB 2/ Optical Port |  |
| 06 | Remote Access | RS232/485 modem interface port |  |
| 07 | Display | Alphanumeric LCD |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 250kVA Distribution Transformer

| Sl. No. | Description |  |  | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer’s Name & Address |  |  | To be mentioned |  |
| 2 | Manufacturer's Type/ Model No. |  |  | To be mentioned |  |
| 3 | KVA Rating |  |  | 250 |  |
| 4 | Number of Phases |  |  | 3 |  |
| 5 | Rated frequency, Hz |  |  | 50 |  |
| 6 | Rated primary voltage, KV |  |  | 11 |  |
| 7 | Rated no load sec. voltage, V |  |  | 415 |  |
| 8 | Vector group |  |  | Dyn11 |  |
| 9 | Highest system voltage of : |  |  |  |  |
|  | a) Primary winding, KV |  |  | 12 |  |
|  | b) Secondary winding, V |  |  | 457 |  |
| 10 | Basic insulation level, KV |  |  | 75 |  |
| 11 | Power frequency withstand voltage, KV |  |  |  |  |
|  | a) HT Side |  |  | 28 |  |
|  | b) LT Side |  |  | 2.5 |  |
| 12 | Type of cooling |  |  | ONAN |  |
| 13 | Max. Temp. Rise over 400C of ambient supported by Calculation (to be submitted) of Load Loss, Temperature Rise and Heat Dissipation by Radiator on the basis of Design Data: |  |  |  |  |
|  | a) Windings deg. C |  |  | 65 |  |
|  | b) Top oil deg. C |  |  | 60 |  |
| 14 | Type of primary tapping off load, % |  |  | +1x2.5%, 0, -3x 2.5% |  |
| 15 | Percentage Impedance at 75o C, % (supported by type test report) |  |  | 4% |  |
| 16 | No-load loss, Watts (supported by type test report) |  |  | 520 |  |
| 17 | Load losses at rated full load at 750C, Watts (supported by type test report) |  |  | 3180 |  |
| 18 | Magnetising current at normal voltage, Amps |  |  | To be mentioned |  |
| 19 | Efficiency at 750C and 100% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  |  | To be mentioned |  |
|  | b) at 0.8 power factor, % |  |  | To be mentioned |  |
| 20 | Efficiency at 750C and 75% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  |  | To be mentioned |  |
|  | b) at 0.8 power factor, % |  |  | To be mentioned |  |
| 21 | Efficiency at 750C and 50% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  |  | To be mentioned |  |
|  | b) at 0.8 power factor, % |  |  | To be mentioned |  |
| 22 | Efficiency at 750C and 25% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  |  | To be mentioned |  |
|  | b) at 0.8 power factor, % |  |  | To be mentioned |  |
| 23 | Regulation at full load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  |  | To be mentioned |  |
|  | b) at 0.8 power factor, % |  |  | To be mentioned |  |
|  | Transformer Oil : |  |  |  |  |
| 24 | a) Type of oil |  |  | Mineral Insulating Oil |  |
|  | b) Manufacturer’s Name & Address |  |  | To be mentioned |  |
| 25 | Total weight of oil, Kg |  |  | To be mentioned |  |
| 26 | Breakdown Voltage at 2.5mm gap between electrodes |  |  | > 50 kV |  |
|  | Transformer Core (Stack Core or Wound Core): |  |  |  |  |
| 27 | Manufacturer’s Name & Address |  |  | To be mentioned |  |
| 28 | Total weight of core, Kg |  |  | To be mentioned |  |
| 29 | Material of core & grading (CRGO/Amorphos) |  |  | To be mentioned |  |
| 30 | Core Loss/ Kg, supported by Characteristic Curve& Core Manufacturer's Brochure |  |  | To be mentioned |  |
| 31 | Thickness of core, mm |  |  | To be mentioned |  |
| 32 | Core Dia, mm |  |  | To be mentioned |  |
| 33 | Max. magnetic flux density, Tesla |  |  | To be mentioned |  |
|  | Transformer Windings : |  |  |  |  |
| 34 | Copper Conductor's Manufacturer Name & Address |  |  | To be mentioned |  |
| 35 | Material of windings |  |  | copper |  |
| 36 | Winding resistance of : |  |  |  |  |
|  | a) H.T. winding, Ohm. (per phase at 75o C) |  |  | To be mentioned |  |
|  | b) L.T. winding, milli-Ohm. (per phase at 75o C) |  |  | To be mentioned |  |
| 37 | Current density of : |  |  |  |  |
|  | a) H.T. winding, Amps/sq. mm |  |  | To be mentioned |  |
|  | b) L.T. winding, Amps/sq. mm |  |  | To be mentioned |  |
| 38 | Outer, Inner & Mean dia of copper winding: |  |  |  |  |
|  | a) H.T. winding, mm |  |  | To be mentioned |  |
|  | b) L.T. winding, mm |  |  | To be mentioned |  |
| 39 | Size of Copper Conductor : |  |  |  |  |
|  | a) H.T. winding SWG, dia. in mm & area in mm2 |  |  | To be mentioned |  |
|  | b) L.T. winding SWG, area in mm2 |  |  | To be mentioned |  |
| 40 | Number of Turns : |  |  |  |  |
|  | a) HT winding, nos. |  |  | To be mentioned |  |
|  | b) LT winding, nos. |  |  | To be mentioned |  |
| 41 | Copper weight of windings : |  |  |  |  |
|  | a) HT winding, Kg |  |  | To be mentioned |  |
|  | b) LT winding, Kg |  |  | To be mentioned |  |
| 42 | Total weight of copper windings, Kg |  |  | To be mentioned |  |
| 43 | Dimension of Transformer : |  |  |  |  |
|  | a) Width, mm (supported by type test report) |  |  | To be mentioned |  |
|  | b) Length, mm (supported by type test report) |  |  | To be mentioned |  |
|  | c) Height, mm (supported by type test report) |  |  | To be mentioned |  |
|  | d) Tank Sheet thickness of top, bottom & side, mm |  |  | 5, 5 & 4 |  |
|  | e) Total weight of transformer tank, Kg |  |  | To be mentioned |  |
| 44 | a) Total weight of active part (core, coil and other accessories), Kg |  |  | To be mentioned |  |
|  | b) Total weight of complete Transformer including fittings & oil, Kg (supported by type test report) |  |  | To be mentioned |  |
| 45 | Type of breathings |  |  | To be mentioned |  |
| 46 | Name of relevant IEC or other Equivalent Standards for Design, manufacture, testing and performance. |  |  | To be mentioned |  |
| 47 | Drawing : |  |  |  |  |
|  | a) | General Arrangement & Outline Dimensions |  | To be submitted |  |
|  | b) | Internal Construction Details/ Sectional drawing of active parts including Insulation arrangement |  | To be submitted |  |
|  | c) | HT & LT Bushings with dimension & current ratings |  | To be submitted |  |
|  | d) | Cross-section &Dimensional drawing of Core & Windings |  | To be submitted |  |
|  | e) | Radiator with detail dimensional drawing |  | To be submitted |  |
|  | f) | Tap changer with dimension & current ratings. |  | To be submitted |  |
| 48 | Routine Test Report : |  |  |  |  |
|  | a) | Measurement of turn ratio test. |  | To be submitted |  |
|  | b) | Vector group test. |  | To be submitted |  |
|  | c) | Measurement of winding resistance. |  | To be submitted |  |
|  | d) | Measurement of insulation resistance. |  | To be submitted |  |
|  | e) | Measurement of no load loss & no-load current. |  | To be submitted |  |
|  | f) | Measurement of impedance voltage & load loss. |  | To be submitted |  |
|  | g) | Dielectric withstands Tests. |  | To be submitted |  |
|  | h) | Transformer oil test (including Tan delta). |  | To be submitted |  |
| 49 | Type Tests report along with details test result and drawings for 11/0.415KV, 250KVA, 3-Phase, Dyn11 Distribution Transformer from an independent testing Laboratoryas per IEC 60076 Standards. |  |  |  |  |
|  | a) | Impulse Voltage Withstands test. |  | To be submitted |  |
|  | b) | Temperature Rise test. |  | To be submitted |  |
| 50 | Short-circuit Tests Report for the offered 11/0.415KV, 250KVA, 3-Phase, Dyn11 Distribution Transformer as per relevant IEC with detail test results & drawings from reputed independent testing Laboratory/ Institution and detail calculation on the basis of design data by the manufacturer. |  |  | To be submitted |  |
| Seal and Signature of the manufacturer: |  |  |  | Seal and Signature of the Bidder: |  |  |

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 100kVA Distribution Transformer

| Sl. No. | Description |  | Purchaser's Requirement |  | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 2 | Manufacturer's Type/ Model No. |  | To be mentioned |  |  |
| 3 | KVA Rating |  | 100 |  |  |
| 4 | Number of Phases |  | 3 |  |  |
| 5 | Rated frequency, Hz |  | 50 |  |  |
| 6 | Rated primary voltage, KV |  | 11 |  |  |
| 7 | Rated no load sec. voltage, V |  | 415 |  |  |
| 8 | Vector group |  | Dyn11 |  |  |
| 9 | Highest system voltage of : |  |  |  |  |
|  | a) Primary winding, KV |  | 12 |  |  |
|  | b) Secondary winding, V |  | 457 |  |  |
| 10 | Basic insulation level, KV |  | 75 |  |  |
| 11 | Power frequency withstand voltage, KV |  |  |  |  |
|  | a) HT Side |  | 28 |  |  |
|  | b) LT Side |  | 2.5 |  |  |
| 12 | Type of cooling |  | ONAN |  |  |
| 13 | Max. Temp. Rise over 400C of ambient supported by Calculation (to be submitted) of Load Loss, Temperature Rise and Heat Dissipation by Radiator on the basis of Design Data: |  |  |  |  |
|  | a) Windings deg. C |  | 65 |  |  |
|  | b) Top oil deg. C |  | 60 |  |  |
| 14 | Type of primary tapping off load, % |  | +1x2.5%, 0, -3x 2.5% |  |  |
| 15 | Percentage Impedance at 75o C, % (supported by type test report) |  | 4% |  |  |
| 16 | No-load loss, Watts (supported by type test report) |  | 245 |  |  |
| 17 | Load losses at rated full load at 750C, Watts (supported by type test report) |  | 1635 |  |  |
| 18 | Magnetising current at normal voltage, Amps |  | To be mentioned |  |  |
| 19 | Efficiency at 750C and 100% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 20 | Efficiency at 750C and 75% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 21 | Efficiency at 750C and 50% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 22 | Efficiency at 750C and 25% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 23 | Regulation at full load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| Transformer Oil : |  |  |  |  |  |
| 24 | a) Type of oil |  | Mineral Insulating Oil |  |  |
|  | b) Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 25 | Total weight of oil, Kg |  | To be mentioned |  |  |
| 26 | Breakdown Voltage at 2.5mm gap between electrodes |  | > 50 kV |  |  |
| Transformer Core (Stack Core or Wound Core): |  |  |  |  |  |
| 27 | Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 28 | Total weight of core, Kg |  | To be mentioned |  |  |
| 29 | Material of core & grading (CRGO/Amorphos) |  | To be mentioned |  |  |
| 30 | Core Loss/ Kg, supported by Characteristic Curve& Core Manufacturer's Brochure |  | To be mentioned |  |  |
| 31 | Thickness of core, mm |  | To be mentioned |  |  |
| 32 | Core Dia, mm |  | To be mentioned |  |  |
| 33 | Max. magnetic flux density, Tesla |  | To be mentioned |  |  |
|  | Transformer Windings : |  |  |  |  |
| 34 | Copper Conductor's Manufacturer Name & Address |  | To be mentioned |  |  |
| 35 | Material of windings |  | copper |  |  |
| 36 | Winding resistance of : |  |  |  |  |
|  | a) H.T. winding, Ohm. (per phase at 75o C) |  | To be mentioned |  |  |
|  | b) L.T. winding, milli-Ohm. (per phase at 75o C) |  | To be mentioned |  |  |
| 37 | Current density of : |  |  |  |  |
|  | a) H.T. winding, Amps/sq. mm |  | To be mentioned |  |  |
|  | b) L.T. winding, Amps/sq. mm |  | To be mentioned |  |  |
| 38 | Outer, Inner & Mean dia of copper winding: |  |  |  |  |
|  | a) H.T. winding, mm |  | To be mentioned |  |  |
|  | b) L.T. winding, mm |  | To be mentioned |  |  |
| 39 | Size of Copper Conductor : |  |  |  |  |
|  | a) H.T. winding SWG, dia. in mm & area in mm2 |  | To be mentioned |  |  |
|  | b) L.T. winding SWG, area in mm2 |  | To be mentioned |  |  |
| 40 | Number of Turns : |  |  |  |  |
|  | a) HT winding, nos. |  | To be mentioned |  |  |
|  | b) LT winding, nos. |  | To be mentioned |  |  |
| 41 | Copper weight of windings : |  |  |  |  |
|  | a) HT winding, Kg |  | To be mentioned |  |  |
|  | b) LT winding, Kg |  | To be mentioned |  |  |
| 42 | Total weight of copper windings, Kg |  | To be mentioned |  |  |
| 43 | Dimension of Transformer : |  |  |  |  |
|  | a) Width, mm (supported by type test report) |  | To be mentioned |  |  |
|  | b) Length, mm (supported by type test report) |  | To be mentioned |  |  |
|  | c) Height, mm (supported by type test report) |  | To be mentioned |  |  |
|  | d) Tank Sheet thickness of top, bottom & side, mm |  | 4, 3 & 3 |  |  |
|  | e) Total weight of transformer tank, Kg |  | To be mentioned |  |  |
| 44 | a) Total weight of active part (core, coil and other accessories), Kg |  | To be mentioned |  |  |
|  | b) Total weight of complete Transformer including fittings & oil, Kg (supported by type test report) |  | To be mentioned |  |  |
| 45 | Type of breathings |  | To be mentioned |  |  |
| 46 | Name of relevant IEC or other Equivalent Standards for Design, manufacture, testing and performance. |  | To be mentioned |  |  |
| 47 | Drawing : |  |  |  |  |
|  | a) | General Arrangement & Outline Dimensions | To be submitted |  |  |
|  | b) | Internal Construction Details/ Sectional drawing of active parts including Insulation arrangement | To be submitted |  |  |
|  | c) | HT & LT Bushings with dimension & current ratings | To be submitted |  |  |
|  | d) | Cross-section &Dimensional drawing of Core & Windings | To be submitted |  |  |
|  | e) | Radiator with detail dimensional drawing | To be submitted |  |  |
|  | f) | Tap changer with dimension & current ratings. | To be submitted |  |  |
| 48 | Routine Test Report : |  |  |  |  |
|  | a) | Measurement of turn ratio test. | To be submitted |  |  |
|  | b) | Vector group test. | To be submitted |  |  |
|  | c) | Measurement of winding resistance. | To be submitted |  |  |
|  | d) | Measurement of insulation resistance. | To be submitted |  |  |
|  | e) | Measurement of no load loss & no-load current. | To be submitted |  |  |
|  | f) | Measurement of impedance voltage & load loss. | To be submitted |  |  |
|  | g) | Dielectric withstands Tests. | To be submitted |  |  |
|  | h) | Transformer oil test (including Tan delta). | To be submitted |  |  |
| 49 | Type Tests report along with details test result and drawings for 11/0.415KV, 100KVA, 3-Phase, Dyn11 Distribution Transformer from an independent testing Laboratoryas per IEC 60076 Standards. |  |  |  |  |
|  | a) | Impulse Voltage Withstands test. | To be submitted |  |  |
|  | b) | Temperature Rise test. | To be submitted |  |  |
| 50 | Short-circuit Tests Report for the offered 11/0.415KV, 100KVA, 3-Phase, Dyn11 Distribution Transformer as per relevant IEC with detail test results & drawings from reputed independent testing Laboratory/ Institution and detail calculation on the basis of design data by the manufacturer. |  | To be submitted |  |  |
| Manufacturer’s Seal & Signature |  |  | Bidder’s Seal & Signature |  |  |

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 50kVA Distribution Transformer

| Sl. No. | Description |  | Purchaser's Requirement |  | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 2 | Manufacturer's Type/ Model No. |  | To be mentioned |  |  |
| 3 | KVA Rating |  | 50 |  |  |
| 4 | Number of Phases |  | 3 |  |  |
| 5 | Rated frequency, Hz |  | 50 |  |  |
| 6 | Rated primary voltage, KV |  | 11 |  |  |
| 7 | Rated no load sec. voltage, V |  | 415 |  |  |
| 8 | Vector group |  | Dyn11 |  |  |
| 9 | Highest system voltage of : |  |  |  |  |
|  | a) Primary winding, KV |  | 12 |  |  |
|  | b) Secondary winding, V |  | 457 |  |  |
| 10 | Basic insulation level, KV |  | 75 |  |  |
| 11 | Power frequency withstand voltage, KV |  |  |  |  |
|  | a) HT Side |  | 28 |  |  |
|  | b) LT Side |  | 2.5 |  |  |
| 12 | Type of cooling |  | ONAN |  |  |
| 13 | Max. Temp. Rise over 400C of ambient supported by Calculation (to be submitted) of Load Loss, Temperature Rise and Heat Dissipation by Radiator on the basis of Design Data: |  |  |  |  |
|  | a) Windings deg. C |  | 65 |  |  |
|  | b) Top oil deg. C |  | 60 |  |  |
| 14 | Type of primary tapping off load, % |  | +1x2.5%, 0, -3x 2.5% |  |  |
| 15 | Percentage Impedance at 75o C, % (supported by type test report) |  | 4% |  |  |
| 16 | No-load loss, Watts (supported by type test report) |  | 155 |  |  |
| 17 | Load losses at rated full load at 750C, Watts (supported by type test report) |  | 810 |  |  |
| 18 | Magnetising current at normal voltage, Amps |  | To be mentioned |  |  |
| 19 | Efficiency at 750C and 100% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 20 | Efficiency at 750C and 75% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 21 | Efficiency at 750C and 50% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 22 | Efficiency at 750C and 25% load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
| 23 | Regulation at full load : |  |  |  |  |
|  | a) at 1.0 power factor, % |  | To be mentioned |  |  |
|  | b) at 0.8 power factor, % |  | To be mentioned |  |  |
|  | Transformer Oil : |  |  |  |  |
| 24 | a) Type of oil |  | Mineral Insulating Oil |  |  |
|  | b) Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 25 | Total weight of oil, Kg |  | To be mentioned |  |  |
| 26 | Breakdown Voltage at 2.5mm gap between electrodes |  | > 50 kV |  |  |
|  | Transformer Core (Stack Core or Wound Core): |  |  |  |  |
| 27 | Manufacturer’s Name & Address |  | To be mentioned |  |  |
| 28 | Total weight of core, Kg |  | To be mentioned |  |  |
| 29 | Material of core & grading (CRGO/Amorphos) |  | To be mentioned |  |  |
| 30 | Core Loss/ Kg, supported by Characteristic Curve& Core Manufacturer's Brochure |  | To be mentioned |  |  |
| 31 | Thickness of core, mm |  | To be mentioned |  |  |
| 32 | Core Dia, mm |  | To be mentioned |  |  |
| 33 | Max. magnetic flux density, Tesla |  | To be mentioned |  |  |
|  | Transformer Windings : |  |  |  |  |
| 34 | Copper Conductor's Manufacturer Name & Address |  | To be mentioned |  |  |
| 35 | Material of windings |  | copper |  |  |
| 36 | Winding resistance of : |  |  |  |  |
|  | a) H.T. winding, Ohm. (per phase at 75o C) |  | To be mentioned |  |  |
|  | b) L.T. winding, milli-Ohm. (per phase at 75o C) |  | To be mentioned |  |  |
| 37 | Current density of : |  |  |  |  |
|  | a) H.T. winding, Amps/sq. mm |  | To be mentioned |  |  |
|  | b) L.T. winding, Amps/sq. mm |  | To be mentioned |  |  |
| 38 | Outer, Inner & Mean dia of copper winding: |  |  |  |  |
|  | a) H.T. winding, mm |  | To be mentioned |  |  |
|  | b) L.T. winding, mm |  | To be mentioned |  |  |
| 39 | Size of Copper Conductor : |  |  |  |  |
|  | a) H.T. winding SWG, dia. in mm & area in mm2 |  | To be mentioned |  |  |
|  | b) L.T. winding SWG, area in mm2 |  | To be mentioned |  |  |
| 40 | Number of Turns : |  |  |  |  |
|  | a) HT winding, nos. |  | To be mentioned |  |  |
|  | b) LT winding, nos. |  | To be mentioned |  |  |
| 41 | Copper weight of windings : |  |  |  |  |
|  | a) HT winding, Kg |  | To be mentioned |  |  |
|  | b) LT winding, Kg |  | To be mentioned |  |  |
| 42 | Total weight of copper windings, Kg |  | To be mentioned |  |  |
| 43 | Dimension of Transformer : |  |  |  |  |
|  | a) Width, mm (supported by type test report) |  | To be mentioned |  |  |
|  | b) Length, mm (supported by type test report) |  | To be mentioned |  |  |
|  | c) Height, mm (supported by type test report) |  | To be mentioned |  |  |
|  | d) Tank Sheet thickness of top, bottom & side, mm |  | 4, 3 & 3 |  |  |
|  | e) Total weight of transformer tank, Kg |  | To be mentioned |  |  |
| 44 | a) Total weight of active part (core, coil and other accessories), Kg |  | To be mentioned |  |  |
|  | b) Total weight of complete Transformer including fittings & oil, Kg (supported by type test report) |  | To be mentioned |  |  |
| 45 | Type of breathings |  | To be mentioned |  |  |
| 46 | Name of relevant IEC or other Equivalent Standards for Design, manufacture, testing and performance. |  | To be mentioned |  |  |
| 47 | Drawing : |  |  |  |  |
|  | a) | General Arrangement & Outline Dimensions | To be submitted |  |  |
|  | b) | Internal Construction Details/ Sectional drawing of active parts including Insulation arrangement | To be submitted |  |  |
|  | c) | HT & LT Bushings with dimension & current ratings | To be submitted |  |  |
|  | d) | Cross-section &Dimensional drawing of Core & Windings | To be submitted |  |  |
|  | e) | Radiator with detail dimensional drawing | To be submitted |  |  |
|  | f) | Tap changer with dimension & current ratings. | To be submitted |  |  |
| 48 | Routine Test Report : |  |  |  |  |
|  | a) | Measurement of turn ratio test. | To be submitted |  |  |
|  | b) | Vector group test. | To be submitted |  |  |
|  | c) | Measurement of winding resistance. | To be submitted |  |  |
|  | d) | Measurement of insulation resistance. | To be submitted |  |  |
|  | e) | Measurement of no load loss & no-load current. | To be submitted |  |  |
|  | f) | Measurement of impedance voltage & load loss. | To be submitted |  |  |
|  | g) | Dielectric withstands Tests. | To be submitted |  |  |
|  | h) | Transformer oil test (including Tan delta). | To be submitted |  |  |
| 49 | Type Tests report along with details test result and drawings for 11/0.415KV, 50KVA, 3-Phase, Dyn11 Distribution Transformer from an independent testing Laboratory as per IEC 60076 Standards. |  |  |  |  |
|  | a) | Impulse Voltage Withstands test. | To be submitted |  |  |
|  | b) | Temperature Rise test. | To be submitted |  |  |
| 50 | Short-circuit Tests Report for the offered 11/0.415KV, 50KVA, 3-Phase, Dyn11 Distribution Transformer as per relevant IEC with detail test results & drawings from reputed independent testing Laboratory/ Institution and detail calculation on the basis of design data by the manufacturer. |  | To be submitted |  |  |
| Manufacturer’s Seal & Signature |  |  | Bidder’s Seal & Signature |  |  |

- Guaranteed Technical Particulars (GTP) of 11/0.4kV, 10kVA Distribution Transformer

| Sl. No. | Technical Particulars | BPDB'S Requirement |  | Manufacturer's Particulars |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer's Name& Address | To be mentioned |  |  |
| 2 | Design standard | ANSI C57.12.00 , C57.12.20 & C57.12.90 (Revisions from 2010 to the latest revision ) |  |  |
| 3 | Type | Single-phase wound core |  |  |
| 4 | KVA Rating | 10KVA |  |  |
| 5 | Winding material | High conductivity Cu |  |  |
| 6 | Core material | Cold Rolled Grain Oriented Silicon Strip Steel(CRGO)/Amorphos |  |  |
| 7 | Nominal voltage | HT = 6350V |  |  |
|  |  | LT = 240V |  |  |
| 8 | BIL | HT winding = 95 KV |  |  |
|  |  | LT winding = 30 KV or as per latest ANSI requirement |  |  |
| 9 | % impedance at rated KVA ( For 5 KVA to 37.5 KVA ) | 2.5% (with + 10% Tolerance ) |  |  |
| 10 | Polarity | Additive |  |  |
| 11 | Cooling method | Class- OA (Self-cooled) |  |  |
| 12 | Temperature rise: |  |  |  |
|  | a) Winding | Shall not exceed 650C (Resistance method) |  |  |
|  | b) Insulating liquid | Shall not exceed 650C |  |  |
| 13 | Bushings |  |  |  |
|  | a) Type & material | Out door type, Porcelain |  |  |
|  | b) Connectors | Bolted ring type |  |  |
|  | c) Quantity | HT = 1, LT = 2 |  |  |
|  | d) Mounting position | HT-on the tank cover |  |  |
|  |  | LT- on the tank side |  |  |
| 14 | Tank |  |  |  |
|  | a) Design | Sealed type complete with cover & gasket |  |  |
|  | b) Grd. Provision | With bolted ring type connector |  |  |
|  | c) LV grd. Provision | With removable Cu strap |  |  |
|  | d) Lifting facilities | Facilities for lifting the core & coil |  |  |
|  | e) Support lug | Shall have support lugs |  |  |
|  | f) Pressure release device | Self sealing pressure release device |  |  |
|  | g) Min.size (dxh) (mm) | As per table - 2 of specification |  |  |
|  | h) Painting | Light Gray, ANSI Color # 70 |  |  |
| 15 | Insulating Oil | New, unused, mineral oil as per ANSI/ASTM D3487-79 |  |  |
| 16 | Guaranteed Load loss in Watt at rated voltage of 850C : |  |  |  |
|  | a) 1/2 load | To be mentioned |  |  |
|  | b) 3/4 load | To be mentioned |  |  |
|  | c) Full load | To be mentioned |  |  |
| 17 | Guaranteed No load loss in Watt | To be mentioned |  |  |
| 18 | Core Loss , watt/kg (supported by loss curve ) | To be mentioned |  |  |
| 19 | HT & LT Weight of Copper with percent of purity. | To be mentioned |  |  |
| 20 | HT & LT Conductor Sizes (Dia in mm & Area in sq.mm | To be mentioned |  |  |
| 21 | Current Densities ( in Amps / sq.mm ) | To be mentioned |  |  |
| 22 | Number of Turns at HT & LT Side | To be mentioned |  |  |
| 23 | Excitation current in Amp | To be mentioned |  |  |
| 24 | Regulation at unity & 0.8 P.F | To be mentioned |  |  |
| 25 | Full load current in amp | To be mentioned |  |  |
| 26 | % Resistance at rated KVA | To be mentioned |  |  |
| 27 | Efficiency at unity P.F. | To be mentioned |  |  |
|  | a) 1/2 load |  |  |  |
|  | b) 3/4 load |  |  |  |
|  | c) Full load |  |  |  |
| 28 | Weight in Kg. | To be mentioned |  |  |
|  | a) with oil |  |  |  |
|  | b) without oil |  |  |  |
| 29 | Drawing showing general arrangement and out line dimension. | To be submitted with the offer. |  |  |
| 30 | Test Reports |  |  |  |
|  | a) Routine test | Test reports must be submitted for the offered transformer. As per ANSI Standard ANSI C57.12.00 , C57.12.20 & C57.12.90 ( Revisions from 2010 to the latest revision ) |  |  |
|  | b) Temperature rise test |  |  |  |
|  | c) Impulse test |  |  |  |
|  | d) Short circuit test |  |  |  |
| 31 | Loss value from test report | To be filled up from test report |  |  |
|  | a) No load loss in KW |  |  |  |
|  | b) Full load loss in KW at 850C |  |  |  |
| 32 | Test Lab. | Should be reputed Independent Testing Laboratory |  |  |
| 33 | Packing & Shipping Box | Packing shall be as per specification and Shipping box shall be per design no. 2 of Exhibit E-2 of bid document. |  |  |
| Manufacturer’s Seal & Signature |  |  | Bidder’s Seal & Signature |  |  |

- Guaranteed Technical Particulars (GTP) of Switchgear, Control & Protection Panel

| Sl No | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1. | Description of the Item | MV Switchgear and Metering Panel |  |
| 2. | Standard | Relevant ANSI / IEC Standard |  |
| 3. | System nominal voltage kV | 11 |  |
| 4. | Maximum System Voltage, kV | 12 |  |
| 5. | Rated Frequency Hz | 50 |  |
| A | Vacuum Circuit Breaker of 630 A |  |  |
|  | Description of the Item | Vacuum Circuit Breaker |  |
|  | Certifications | To be mentioned |  |
|  | Model Number | To be mentioned |  |
|  | Rated Frequency | 50 Hz |  |
|  | Rated Nominal Voltage | 33 kV |  |
|  | Maximum Rated Voltage | 36 kV |  |
|  | Rated Nominal Current | 630 A |  |
|  | Number of Breaks Per Phase | To be mentioned |  |
|  | Interrupting Medium | Vacuum |  |
|  | Insulation | SF6 |  |
|  | Basic Insulation Level | 170 kV peak (1.2/50 µs) |  |
|  | Power Frequency Withstand Voltage | 70 kV (For 1 Minute @ 50 Hz) |  |
| B | Vacuum Circuit Breaker of 1250A |  |  |
|  | Description of the Item | Vacuum Circuit Breaker |  |
|  | Certifications | To be mentioned |  |
|  | Model Number | To be mentioned |  |
|  | Rated Frequency | 50 Hz |  |
|  | Rated Nominal Voltage | 33 kV |  |
|  | Maximum Rated Voltage | 36 kV |  |
|  | Rated Nominal Current | 1250 A |  |
|  | Number of Breaks Per Phase | To be mentioned |  |
|  | Interrupting Medium | Vacuum |  |
|  | Insulation | SF6 |  |
|  | Basic Insulation Level | 170 kV peak (1.2/50 µs) |  |
|  | Power Frequency Withstand Voltage | 70 kV (For 1 Minute @ 50 Hz) |  |
| C. PROTECTION CONTROL & METERING |  |  |  |
| 6. | Differential Relay |  |  |
|  | Manufacturer’s Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of Relay | Numerical programmable |  |
|  | The Relay protocol | IEC 61850 type |  |
| 7. | Restricted Earth Fault Relay |  |  |
|  | Manufacture's Name & Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of Relay | Numerical programmable |  |
|  | The Relay protocol | IEC 61850 type |  |
| 8 | IDMT OVER CURRENT & EARTH FAULT RELAY |  |  |
|  | Manufacture's Name Country of Origin | To be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of relay | Numerical programmable Multifunction |  |
|  | The Relay protocol | IEC 61850 type |  |
| 9 | Separate Auxiliary Flag Relays for Transformer self-protection (OTA, OTT, WTA, WTT, BA, BT, OLTC Surge, PRD for main tank. |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no | Shall be mentioned |  |
|  | Type of Relays | Shall be mentioned |  |
| 10 | Trip Circuit Supervision (TCS) Relay (Separate Relay for each trip coil) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of Relay | Shall be mentioned |  |
| 11 | Trip Relay (Separate Relay) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Operating Time, ms | <10 |  |
|  | Self-reset type for O/C, E/F protection | Yes |  |
|  | Hand & Electrical reset type for Differential, REF and Transformer Self-protection | Yes |  |
| 12 | Annunciator |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Windows, nos. | 24 |  |
|  | Built in buzzer and buttons for accept, mute, test, reset, etc. | Yes |  |
| 13 | Control Switch |  |  |
|  | Manufacture's Name & Country | Shall be mentioned |  |
|  | Manufacture's Model/Type No. | Shall be mentioned |  |
|  | Separate TNC/Discrepancy switch and Local Remote (L/R) selector switch | Yes |  |
| 14 | AVR Relay: Transformer incomer PCM panel shall be equipped with AVR relay and control switch for RTCC operation along with necessary indication system (Tap position, oil temperature, winding temperature etc.). | Yes |  |
| 20 | METERING AND INSTRUMENTATION |  |  |
| 20.1 | KWH & kVARH Meter |  |  |
|  | Manufacture’s Name & Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Numerical programmable Multifunction |  |
|  | Class of Accuracy | 0.2 |  |
| 20.2 | VOLT METERS with Selector Switch |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 90 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
| 20.3 | AMPERE METERS |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 240 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
|  | Separate A-meter for each phase | Yes |  |
|  | Mega Watt (MW) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 20.4 | Mega VAR (MVAR) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 21 | The PCM Panel Shall be complied all the technical specification mentioned in Section-6. | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of PCMS Server

| SL. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| PCMS Server |  |  |  |
|  | Manufacturer | To be mentioned |  |
|  | Country of origin | To be mentioned |  |
|  | Type | To be mentioned |  |
|  | Standards | IEC |  |
|  | Type of housing | Industrial 19" rack |  |
| Characteristics |  |  |  |
|  | Auxiliary supply voltage | To be mentioned |  |
|  | Rated auxiliary supply voltage, V d.c. | To be mentioned |  |
|  | Dual power supply | Yes |  |
|  | Processor type | To be mentioned |  |
|  | Processor clock, GHz | To be mentioned |  |
|  | Memory type | To be mentioned |  |
|  | Memory capacity, MB | To be mentioned |  |
|  | Video display adapter type | To be mentioned |  |
|  | Video display adapter memory | To be mentioned |  |
|  | Hard disc type | To be mentioned |  |
|  | Rotating hard disc, Yes/No | To be mentioned |  |
|  | Hard disc capacity, GB | To be mentioned |  |
|  | Number of hard discs, pcs. | To be mentioned |  |
|  | RAID controller type | To be mentioned |  |
|  | DVD RW type | To be mentioned |  |
|  | Serial interface RS232 | Yes |  |
|  | Number of serial interfaces | Min. 2 |  |
|  | Fast Ethernet network interface card type | To be mentioned |  |
|  | Number of fast Ethernet network interface cards, pcs. | 4 |  |
|  | Fans , Yes/No | Insert |  |
|  | Monitor 19", pcs. | 1 |  |
|  | Manufacturer | To be mentioned |  |
|  | Country of origin | To be mentioned |  |
|  | Type , TFT | To be mentioned |  |
|  | Standards | IEC |  |
|  | Supply voltage | To be mentioned |  |
|  | Rated auxiliary supply voltage, Va.c | To be mentioned |  |
|  | Power consumption, W | To be mentioned |  |
|  | Vertical frequency, Hz | To be mentioned |  |
|  | Max. resolution | To be mentioned |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of PCMS /EMS Software(Open Source Software)

| No. | Description | Minimum Requirements |  | Guaranteed |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
|  | PCMS Software |  |  |  |
| 1. Basic PCMS server software |  |  |  |  |
|  | Basic PCMS server software | pcs. | 2 |  |
|  | Communication with 2 higher level control centres |  | Yes |  |
|  | Real-time database management |  | Yes |  |
|  | Data processing |  | Yes |  |
|  | Data acquisition |  | Yes |  |
|  | Alarm and event processing |  | Yes |  |
|  | Data archiving |  | Yes |  |
|  | Report generation and printing |  | Yes |  |
|  | Redundancy management |  | Yes |  |
| 2. Operator workstation software |  | pcs. | 2 |  |
| 3. Communication software |  | pcs. | 2 |  |
|  | Communication with 2 higher level control centres |  | Yes |  |
| 4. Application libraries |  | pcs. | 1, optional |  |
| 5. Software tools |  | pcs. | 1 |  |
|  | Database creating, maintaining and viewing |  | Yes |  |
|  | User interface definition |  | Yes |  |
|  | Report definition |  | Yes |  |
|  | System configuration |  | Yes |  |
|  | Historical data maintaining |  | Yes |  |
|  | Database and historical data export/import |  | Yes |  |
|  | Analysis and diagnostic tools |  | Yes |  |
|  | Training simulator |  | Yes |  |
|  | Other software tools according to Contractor's concept: |  | Insert |  |
| Manufacturer’s Seal & Signature |  |  | Bidder’s Seal & Signature |  |

- Guaranteed Techncial Particulars ( GTP) for EMS

| Sl. No | Description | Minimum Requirements | Guaranteed |
| --- | --- | --- | --- |
| 1 | Hardware interoperability | The hardware’s/controller for BESS, PV and Diesel Generator must be interoperable and |  |
| 2 | Plant Control | Ability to control BESS, solar PV plant and generator under all their intended control modes including black start Maximize sustainable power penetration in all control mode Complete system checks of each subsystem for safe operation of the system Log all faults and generate Alarm Able to operate the plant in 100% RE mode Remotely accessible via GSM |  |
| 3 | BESS Control | Capability to adapt BESS SoC limits when load shifting to ensure full local-grid support functionality at all times The EMS BESS controller capable of transforming the BESS operating mode between grid-forming or grid-following and also able to run in droop mode (acting as a virtual synchronous generator) |  |
| 4 | Generator Control | Capability to adapt to different configurations of generator (s) (including outages for maintenance) while ensuring redundancy requirements are met. Provision for accommodating typical response times of connected generator(s) to dispatch commands, including start-up of additional generators ( in case of future expansion) |  |
| 5 | PV Generation Plant Control | Capability to adjust Solar output based on Load , Generator set points and BESS set points Capability to use real-time local irradiance data to estimate capacity of curtailed solar PV and utilize this in dynamically allocating spinning reserve. |  |
| 6 | Control Setpoints | Need to have user configurable (tuneable) settings for inputs to dynamic spinning reserve calculation, ramp times, delays, limits, and conditions for state transition. |  |
| 7 | Stand Alone Operations | Be operable as a stand-alone system with Generator, even when the BESS or solar PV is off-line for maintenance. The EMS should also support (prevent disruption of) operations that do not require the BESS and solar PV plant, including black start (ensuring compatible setting of solar PV and BESS state, mode, or other requirement, including their respective switchgear, and communicating status with the thermal system) Be separable, such that the existing thermal power plant can continue to operate if the EMS is off-line |  |
| 8 | Communication | Use Modbus TCP communications and fibre optic connections Be capable of interfacing with remote equipment via optic fiber or 4G communications Be capable of interfacing with solar PV plant with SunSpec protocols, and associated switchgear Be capable of interfacing with other BESS and micro-grid controllers operating in the network (subject to above expectations on interface and communications, and cooperation of the supplier / operator of that equipment); may require definition of a response profile for management of that other equipment |  |
| 9 | HMI | Include a with remote web access capability, also accessible on the power station operator workstation |  |
| 10 | Future Plant Expansion | Provide expansion capability to add or reconfigure BESS, solar PV, or thermal generators over the EMS life (up to 100% of initial connections as spare) The EMS must provide flexibility for future upgrade requirements. Future upgrade requirements may include addition of new generators or configuration changes in the network, or adopting improvements in available EMS software. EMS vendor will be required to offer product support and support for such requirements (which may include remote support and site visits if needed). |  |
| 11 | Software | Open source code for all software shall be utilized wherever this option is available. Open source code shall be provided as a deliverable, including documentation. If proprietary software is utilised, then in the event that an OEM is unable to meet the required commitment to support any proprietary software needed for operations, then this software must be made available to the Employer in a standard, usable, source code form with documentation of such software. Provision to meet this requirement through a third party shall be made in advance (prior to Completion) in the event OEM is unavailable to release software. |  |
| 12 | Weather forecasting predictive operation | To be compatible with leading sky imager solutions, enabling it to predict the weather and PV production and take counter-measures if needed ( in case the BESS has reached its lower setpoint SoC), for example starting up the required number of genset in due time before clouds reduce PV production – and keeping gensets running if forecasts indicate that PV production will drop again shortly. |  |

| Manufacturer’s Seal & Signature | Bidder’s Seal & Signature |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of Battery Charger

| SL No. | Description | Minimum Requirements |  | Guaranteed |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
|  | Manufacturer |  |  |  |
|  | Type designation |  |  |  |
|  | Type |  | Thyristor controlled |  |
|  | Country of origin |  | - |  |
|  | Standards |  | IEC |  |
|  | Rated input voltage | V | 3 x 400 / 230 |  |
|  | Rated input current (at rated output) | A | To be mentioned |  |
|  | Input voltage variation | % | ±5 |  |
|  | Power factor | 1 | > 0,80 |  |
|  | Efficiency | % | > 85 |  |
|  | Degree of protection |  | IP42 |  |
|  | Noise level | dB | < 65 dB max |  |
|  | Type of rectifiers |  | Modular with MCU |  |
|  | Number of modules (n+2) | pcs | To be mentioned |  |
|  | Module rated output current | A | To be mentioned |  |
|  | MCU protocol |  | IEC 61850 |  |
|  | Charging characteristic |  | Both constant current & constant voltage |  |
|  | Rated frequency | Hz | 50 |  |
|  | Insulation - HV, between input and output/ground | V AC, min | 1000 V AC, 1 min |  |
|  | Insulation resistance | MW; V DC, min | 10 MW, 500 V DC, 1 min |  |
|  | Rated capacity | kVA | To be mentioned |  |
|  | Rated output voltage | V d.c. | 220 |  |
|  | Rated output current | A | 100 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Voltage & Frequency variation | % | ±5 |  |
|  | Voltage ripple | % | ±5 |  |
|  | Ripple frequency | Hz | ±2 |  |
|  | Charge modes | - | 3 levels: charge, float & boost |  |
|  | Float voltage per cell | V | 1.42 |  |
|  | Boost voltage per cell | V | 1.53 |  |
|  | Float & Boost voltage adjustable | - | Yes |  |
|  | Measurement |  | Input voltage Output voltage Output current Battery current Load current Earth-fault voltage |  |
| Manufacturer’s Seal & Signature |  | Bidder’s Seal & Signature |  |  |

- Guaranteed Technical Particulars (GTP) of UPS/Battery

| Sl. No. | Item | To be Proposed by the Bidder |
| --- | --- | --- |
|  | Manufacturer |  |
|  | Country of Manufacture |  |
|  | Model |  |
|  | Voltage output (V) |  |
|  | Regulation (± %) |  |
|  | Frequency (Hz) |  |
|  | Power Rating (VA) |  |
|  | Load Power Factor |  |
|  | Load Crest Factor |  |
|  | Transfer Time (ms) |  |
|  | Current (A) |  |
|  | Overload Capability (%) |  |
|  | Waveform |  |
|  | Distortion (< %) |  |
|  | Transient Regulation (± 5%) |  |
| UPS Input |  |  |
|  | Voltage (V) |  |
|  | Voltage Range (+% -%) |  |
|  | Frequency (Hz) |  |
|  | Maximum Current (A) |  |
|  | Power Factor |  |
| UPS Battery |  |  |
|  | Type |  |
|  | Rating (V – Ah) |  |
|  | Number of Cells |  |
|  | Autonomy Time at full load (min) |  |
|  | Recharge Time to 90% capacity as multiple of outage time |  |
| Manufacturer’s Seal & Signature |  | Bidder’s Seal & Signature |

- Guaranteed Technical Particulars for 12M, 450daN Galvanized Telescopic Steel Pole

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item | -- | 12M 450daN, Galvanized Telescopic Steel Pole |  |
| 2 | Name of the Manufacturer | -- | Shall be mentioned |  |
| 3 | Address of the Manufacturer | -- | Shall be mentioned |  |
| 4 | Standard | -- | Performance Design and Testing shall be in accordance to the BS, IEC, ASTM, BDS or equivalent International standards. |  |
| 5 | Manufacturer's code no of pole | -- | Shall be mentioned |  |
| 6 | Overall length | Meter | 12 Meter |  |
| 7 | Depth of Plantation | Meter | 1/6 of the length |  |
| 8 | Tapper Ratio | mm/Meter | Shall be mentioned |  |
| 9 | Number of Sections | nos. | 2 |  |
| 10 | Length of each section | Meter | Shall be mentioned |  |
| 11 | Outside diameter (Top & Bottom) of each section | mm | Shall be mentioned |  |
| 12 | Thickness of each section | mm | Shall be mentioned |  |
| 13 | Overlapping of each section | mm | Shall be mentioned |  |
| 14 | Total Weight of Pole | Kg | Shall be mentioned |  |
| 15 | Minimum Tensile strength of Steel | N/mm2 | Shall be mentioned |  |
| 16 | Minimum Yield strength of Steel | N/mm2 | 280 |  |
| 17 | Galvanization Coating | -- | Hot Dip Galvanized after Fabrication as per BS EN ISO 1461:1999 |  |
| 18 | Type of anti-corrosive paint | -- | Shall be mentioned |  |
| 19 | Thickness of anti-corrosive paint - Outside - Inside | Micron Micron | 2 x 100 1 x 100 |  |
| 20 | Number of Longitudinal Joint per section | nos. | 2 (max) |  |
| 21 | Factor of Safety of Pole on Yield Strength | -- | 2 (min) |  |
| 22 | The Steel Poles shall be complied all the technical specification mentioned in Bid Document. |  | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for 12M, 350daN Galvanized Telescopic Steel Pole

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item | -- | 12M 350daN, Galvanized Telescopic Steel Pole |  |
| 2 | Name of the Manufacturer | -- | Shall be mentioned |  |
| 3 | Address of the Manufacturer | -- | Shall be mentioned |  |
| 4 | Standard | -- | Performance Design and Testing shall be in accordance to the BS, IEC, ASTM, BDS or equivalent International standards. |  |
| 5 | Manufacturer's code no of pole | -- | Shall be mentioned |  |
| 6 | Overall length | Meter | 12 Meter |  |
| 7 | Depth of Plantation | Meter | 1/6 of the length |  |
| 8 | Tapper Ratio | mm/Meter | Shall be mentioned |  |
| 9 | Number of Sections | nos. | 2 |  |
| 10 | Length of each section | Meter | Shall be mentioned |  |
| 11 | Outside diameter (Top & Bottom) of each section | mm | Shall be mentioned |  |
| 12 | Thickness of each section | mm | Shall be mentioned |  |
| 13 | Overlapping of each section | mm | Shall be mentioned |  |
| 14 | Total Weight of Pole | Kg | Shall be mentioned |  |
| 15 | Minimum Tensile strength of Steel | N/mm2 | Shall be mentioned |  |
| 16 | Minimum Yield strength of Steel | N/mm2 | 280 |  |
| 17 | Galvanization Coating | -- | Hot Dip Galvanized after Fabrication as per BS EN ISO 1461:1999 |  |
| 18 | Type of anti-corrosive paint | -- | Shall be mentioned |  |
| 19 | Thickness of anti-corrosive paint - Outside - Inside | Micron Micron | 2 x 100 1 x 100 |  |
| 20 | Number of Longitudinal Joint per section | nos. | 2 (max) |  |
| 21 | Factor of Safety of Pole on Yield Strength | -- | 2 (min) |  |
| 22 | The Steel Poles shall be complied all the technical specification mentioned in Bid Document. |  | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for 9M, 300daN Galvanized Telescopic Steel Pole

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item | -- | 9M 300daN, Galvanized Telescopic Steel Pole |  |
| 2 | Name of the Manufacturer | -- | Shall be mentioned |  |
| 3 | Address of the Manufacturer | -- | Shall be mentioned |  |
| 4 | Standard | -- | Performance Design and Testing shall be in accordance to the BS, IEC, ASTM, BDS or equivalent International standards. |  |
| 5 | Manufacturer's code no of pole | -- | Shall be mentioned |  |
| 6 | Overall length | Meter | 9 Meter |  |
| 7 | Depth of Plantation | Meter | 1/6 of the length |  |
| 8 | Tapper Ratio | mm/Meter | Shall be mentioned |  |
| 9 | Number of Sections | nos. | 2 |  |
| 10 | Length of each section | Meter | Shall be mentioned |  |
| 11 | Outside diameter (Top & Bottom) of each section | mm | Shall be mentioned |  |
| 12 | Thickness of each section | mm | Shall be mentioned |  |
| 13 | Overlapping of each section | mm | Shall be mentioned |  |
| 14 | Total Weight of Pole | Kg | Shall be mentioned |  |
| 15 | Minimum Tensile strength of Steel | N/mm2 | Shall be mentioned |  |
| 16 | Minimum Yield strength of Steel | N/mm2 | 280 |  |
| 17 | Galvanization Coating | -- | Hot Dip Galvanized after Fabrication as per BS EN ISO 1461:1999 |  |
| 18 | Type of anti-corrosive paint | -- | Shall be mentioned |  |
| 19 | Thickness of anti-corrosive paint - Outside - Inside | Micron Micron | 2 x 100 1 x 100 |  |
| 20 | Number of Longitudinal Joint per section | nos. | 2 (max) |  |
| 21 | Factor of Safety of Pole on Yield Strength | -- | 2 (min) |  |
| 22 | The Steel Poles shall be complied all the technical specification mentioned in Bid Document. |  | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for 9M, 200daN Galvanized Telescopic Steel Pole

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item | -- | 9M 200daN, Galvanized Telescopic Steel Pole |  |
| 2 | Name of the Manufacturer | -- | Shall be mentioned |  |
| 3 | Address of the Manufacturer | -- | Shall be mentioned |  |
| 4 | Standard | -- | Performance Design and Testing shall be in accordance to the BS, IEC, ASTM, BDS or equivalent International standards. |  |
| 5 | Manufacturer's code no of pole | -- | Shall be mentioned |  |
| 6 | Overall length | Meter | 9 Meter |  |
| 7 | Depth of Plantation | Meter | 1/6 of the length |  |
| 8 | Tapper Ratio | mm/Meter | Shall be mentioned |  |
| 9 | Number of Sections | nos. | 2 |  |
| 10 | Length of each section | Meter | Shall be mentioned |  |
| 11 | Outside diameter (Top & Bottom) of each section | mm | Shall be mentioned |  |
| 12 | Thickness of each section | mm | Shall be mentioned |  |
| 13 | Overlapping of each section | mm | Shall be mentioned |  |
| 14 | Total Weight of Pole | Kg | Shall be mentioned |  |
| 15 | Minimum Tensile strength of Steel | N/mm2 | Shall be mentioned |  |
| 16 | Minimum Yield strength of Steel | N/mm2 | 280 |  |
| 17 | Galvanization Coating | -- | Hot Dip Galvanized after Fabrication as per BS EN ISO 1461:1999 |  |
| 18 | Type of anti-corrosive paint | -- | Shall be mentioned |  |
| 19 | Thickness of anti-corrosive paint - Outside - Inside | Micron Micron | 2 x 100 1 x 100 |  |
| 20 | Number of Longitudinal Joint per section | nos. | 2 (max) |  |
| 21 | Factor of Safety of Pole on Yield Strength | -- | 2 (min) |  |
| 22 | The Steel Poles shall be complied all the technical specification mentioned in Bid Document. |  | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for ACSR DOG Conductor

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | ACSR DOG |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, ASTM, BDS or equivalent International standards. |  |
| 5 | Installation |  | Overhead |  |
| 6 | Type |  | Stranded |  |
| 7 | Material |  | Hard drawn Aluminium steel reinforced |  |
| 8 | Overall diameter | mm | 14.15 |  |
| 9 | Nominal cross sectional area of conductor | mm2 | 118.47 |  |
| 10 | Number/diameter of Aluminium Strand | No./mm | 6/4.72 |  |
| 11 | Nominal Aluminium cross sectional area | mm2 | 104.93 |  |
| 12 | Number/diameter of Steel Strand | No./mm | 7/1.57 |  |
| 13 | Nominal Steel cross sectional area | mm2 | 13.56 |  |
| 14 | Weight of conductor | Kg/KM | 394 |  |
| 15 | Drum wound length | M | 1700 |  |
| 16 | Net weight | Kg | Shall be mentioned |  |
| 17 | Gross weight | Kg | Shall be mentioned |  |
| 18 | Maximum DC Resistance of Conductor at 20 °C | /KM | 0.2733 |  |
| 19 | Minimum breaking Load of Conductor | Kg | 3335 |  |
| 20 | Maximum working tension of conductor | KN | Shall be mentioned |  |
| 21 | Current rating at 35ºC rise over 40ºC ambient temperature (75ºC) | Amps. | 272 (min) |  |
| 22 | Practical (final) modulus of elasticity | hbar | 7500 |  |
| 23 | Co-efficient of linear expansion | /ºC | 19.8 x 10-6 |  |
| 24 | Aluminum to Steel Ratio |  | Shall be mentioned |  |
| 25 | Lay length for Outermost Layer of Aluminium | mm | Shall be mentioned |  |
| 26 | Lay direction for Outermost Layer of Aluminium |  | Right hand |  |
| 27 | Lay ratio for Outermost Layer of Aluminium |  | 10-14 |  |
| 28 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for AAC WASP (Insulated) Conductor

| Sl. No. |  | Unit | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | AAC WASP (Insulated) |  |
| 2 | Description |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, BDS or equivalent International standards. |  |
| 5 | Installation |  | Overhead |  |
| 6 | Type |  | Stranded |  |
| 7 | Material |  | Hard drawn Aluminium |  |
| 8 | Overall diameter | mm | 15.57 |  |
| 9 | Diameter of bare conductor | mm | 13.17 |  |
| 10 | Number/diameter of Aluminium | No./mm | 7/4.39 |  |
| 11 | Nominal cross sectional area of conductors | mm2 | 106.00 |  |
| 12 | Type & Colour of Insulation |  | PVC, Black |  |
| 13 | Insulation thickness (min.) | mm | 0.8 |  |
| 14 | Weight of bare conductor | Kg/KM | 290 |  |
| 15 | Weight of insulated conductor | Kg/KM | 389 |  |
| 16 | Drum wound length | M | 1300 |  |
| 17 | Net weight | Kg | Shall be mentioned |  |
| 18 | Gross weight | Kg | Shall be mentioned |  |
| 19 | Maximum DC Resistance of Conductor at 20 °C | /KM | 0.2702 |  |
| 20 | Minimum breaking Load of Conductor | Kg | 1632 |  |
| 21 | Maximum working tension of conductor | KN | Shall be mentioned |  |
| 22 | Current rating at 35ºC rise over 40ºC ambient temperature (75ºC) | Amps. | 260 (min) |  |
| 23 | Practical (final) modulus of elasticity | hbar | 5900 |  |
| 24 | Co-efficient of linear expansion | /ºC | 2.30 x 10-6 |  |
| 25 | Lay length of Outermost Layer | mm | Shall be mentioned |  |
| 26 | Lay direction of Outermost Layer |  | Right hand |  |
| 27 | Lay ratio of Outermost Layer |  | 10-14 |  |
| 28 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for AAC ANT (Insulated) Conductor

| Sl. No. | Description | Unit | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | AAC ANT (Insulated) |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, BDS or equivalent International standards. |  |
| 5 | Installation |  | Overhead |  |
| 6 | Type |  | Stranded |  |
| 7 | Material |  | Hard drawn Aluminium |  |
| 8 | Overall diameter | mm | 11.70 |  |
| 9 | Diameter of bare conductor | mm | 9.30 |  |
| 10 | Number/diameter of Aluminium | No./mm | 7/3.10 |  |
| 11 | Nominal cross sectional area of conductors | mm2 | 52.84 |  |
| 12 | Type & Colour of Insulation |  | PVC pressure insulation, Black |  |
| 13 | Insulation thickness (min.) | mm | 0.8 |  |
| 14 | Weight of bare conductor | Kg/KM | 145 |  |
| 15 | Weight of insulated conductor | Kg/KM | 200 |  |
| 16 | Drum wound length | M | 2200 |  |
| 17 | Net weight | Kg | Shall be mentioned |  |
| 18 | Gross weight | Kg | Shall be mentioned |  |
| 19 | Maximum DC Resistance of Conductor at 20 °C | /KM | 0.5419 |  |
| 20 | Minimum breaking Load of Conductor | KN | 8.28 |  |
| 21 | Maximum working tension of conductor | KN | Shall be mentioned |  |
| 22 | Current rating at 35ºC rise over 40ºC ambient temperature (75ºC) | Amps. | 172 (min) |  |
| 23 | Practical (final) modulus of elasticity | hbar | 5900 |  |
| 24 | Co-efficient of linear expansion | /ºC | 2.30 x 10-6 |  |
| 25 | Lay length of Outermost Layer | mm | Shall be mentioned |  |
| 26 | Lay direction of Outermost Layer |  | Right hand |  |
| 27 | Lay ratio of Outermost Layer |  | 10-14 |  |
| 28 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) for Platform Structure for Distribution Transformer

| Sl. No. | Description | Purchaser's Requirement | Manufacturer's Guaranteed Data |
| --- | --- | --- | --- |
| 1. | Manufacturer’s Name & address | To be mentioned |  |
| 2. | Materials | Mild Steel |  |
| 3. | Minimum Yield Strength of Material | 245 N/Sq. mm |  |
| 4. | Galvanization | Hot Dip Galvanized as per BS 729 |  |
| 6. | (a) Size of Base Angle | 150 x 100 x 8 x 3000 mm |  |
|  | (b) Size of Fuse Mount Channel | 100 x 50 x 6 x 3000 mm |  |
|  | c) Size of Transformer Base Bracing Angle | 90 x 90 x 6 x 1150 mm |  |
| 7. | Dimension Tolerances: |  |  |
|  | a) Material Size | + 1 mm |  |
|  | b) Thickness | -0%, +10% |  |
| 8. | All Dimensions and Hole Size | Shall be as per Drawing (To be confirmed) |  |
| 9. | Bill of Materials and Dimensions of all other accessories (J-bolt, Clamp for bracing, Clamp for fuse mount channel, Pole band, Nuts and Bolts etc.) | Shall be as per Drawing (To be confirmed) |  |
| 10. | Weight, Kg |  |  |
|  | (a) Base Angle (each) | To be mentioned |  |
|  | (b) Fuse Mount Channel (each) | To be mentioned |  |
|  | c) Transformer Base Bracing Angle (each) | To be mentioned |  |
|  | d) J-bolt (each) | To be mentioned |  |
|  | e) Clamp for bracing (each) | To be mentioned |  |
|  | f) Clamp for fuse mount channel (each) | To be mentioned |  |
|  | g) Pole band (each) | To be mentioned |  |
|  | h) Nuts and Bolts-Type A, M16x50 (each) | To be mentioned |  |
|  | i) Nuts and Bolts-Type A, M16x63 (each) | To be mentioned |  |
|  | j) Nuts and Bolts-Type A, M16x300 (each) | To be mentioned |  |
| 11. | Standards | BS 729, BS 4190, BS 4360, BS 4870 |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) for Disel Generator

| Sl. No. | Description | Purchaser's Requirement | Manufacturer's Guaranteed Data |
| --- | --- | --- | --- |
| 1 | Description of the Item | Diesel Generator Set |  |
| 2 | Battery Charger | Built in Automatic Battery Charger system with Charger failure indicator/voltage level indicator |  |
| 3 | Canopy | Sound proof Canopy. Sound Level: 67db@ 7 meter |  |
| 4 | Design Lifetime | Minimum 20 years |  |
| 5 | Weight and Dimension | To be mentioned |  |
| 6 | Warranty | Minimum 3 years |  |
| Engine |  |  |  |
| 1 | Description of Engine | Internal Combustion Diesel Engine |  |
| 2 | Country of Origin | To be mentioned |  |
| 3 | Name and Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC, BS, BDS or equivalent international standards. |  |
| 5 | Certifications | To be mentioned |  |
| 6 | Model Number | To be mentioned |  |
| 7 | Type of Engine | Compression Ignition Engine |  |
| 8 | Noise at a distance of 100 metres | To be mentioned |  |
| 9 | Engine rated speed, rpm | 1500rpm |  |
| 10 | Critical speed above and below rated speed | To be mentioned |  |
| 11 | Engine Starting System | To be mentioned |  |
| 12 | Max. starting time required from standstill to full speed, min | To be mentioned |  |
| 13 | Max. vibration limit, mm/sec | To be mentioned |  |
| 14 | Number of Cylinders | 6 Nos |  |
| 15 | Type and arrangement of Cylinders | Vertical in Line |  |
| 16 | Number of strokes | 4 Stroke |  |
| 17 | Ignition mode | Compression Ignition |  |
| 18 | Speed Governing system | Mechanical |  |
| 20 | Induction | Turbocharged |  |
| 21 | Fuel consumption | Maximum 32.0 ltr/hr at 75% Load and 42.0 ltr/hr at 100% Load |  |
| 22 | Fuel Tank Capacity | Minimum 350 Litre |  |
| 23 | Lube Oil Tank Capacity | Minimum 15 Litre |  |
| 24 | Cooling System | To be mentioned |  |
| 25 | Weight and Dimension | To be mentioned |  |
| Alternator |  |  |  |
| 1 | Description of Alternator | Three phase AC alternator |  |
| 2 | Country of Origin | To be mentioned |  |
| 3 | Name and Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC, BS, BDS or equivalent international standards. |  |
| 5 | Certifications | To be mentioned |  |
| 6 | Model Number | To be mentioned |  |
| 7 | No of Phase and wire | Three phase, four wire |  |
| 8 | Rated Capacity at Site condition , KVA | Minimum 200 KVA |  |
| 9 | Rated output at 0.85pf | Minimum 170kW |  |
| 10 | Rated Voltage, V | 415 V |  |
| 11 | Frequency, Hz | 50 Hz |  |
| 12 | Excitation System | PMG |  |
| 13 | Voltage Sensing | 2 Phase |  |
| 14 | Material Insulation Class | H |  |
| 15 | Bearing Arrangement | Single |  |
| 16 | Weight and Dimension | To be mentioned |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) Double Cabin Disel Pick Up

| Sl. No. | Description | Purchaser's Requirement | Manufacturer's Guaranteed Data |
| --- | --- | --- | --- |
| 1 | General |  |  |
|  | a) Country of Origin | To be mentioned |  |
|  | b) Country of make | To be mentioned |  |
|  | c) Name of Manufacturer | To be mentioned |  |
|  | d) Year of manufacture | 2024 or latest |  |
|  | e) Model | To be mentioned |  |
|  | f) Brand | To be mentioned |  |
| 2 | Body |  |  |
|  | a) Overall length | To be mentioned |  |
|  | b) Overall width | To be mentioned |  |
|  | c) Overall height | To be mentioned |  |
|  | d) Wheel base | To be mentioned |  |
|  | e) Ground clearance | To be mentioned |  |
|  | f) Total weight | To be mentioned |  |
|  | g) Number of doors | 4(four) |  |
|  | h) Seating Capacity | 5 Seated |  |
|  | i) Loading Capacity (Kg) | 1000 Kg |  |
|  | j) Color | Manufacturer’s standard |  |
|  | k) Drive | Right hand drive (RHD) |  |
| 3 | Engine |  |  |
|  | a) Model | To be mentioned |  |
|  | b) Type | 4- Stroke, 4- cylinder, in line |  |
|  | c) Fuel system | Diesel |  |
|  | d) Fuel tank | 80 Litre (Minimum) |  |
|  | e) Displacement (CC) | 2700 (Minimum) |  |
|  | f) Maximum H.P./RPM | 221 HP @ 3400 RPM |  |
|  | g) Fuel consumption Km/litre | To be mentioned (Fuel consumption curve is preferable) |  |
| 4 | Transmission system |  |  |
|  | a) Transmission System | Part time manual 4x4 |  |
|  | b) Gearbox | Automatic |  |
|  | c) Rear Differential | Manual locking |  |
| 5 | Steering System | Power |  |
| 6 | Brake System |  |  |
|  | Front Brake | Ventilated discs |  |
|  | Rear Brake | Drums |  |
|  | Parking Brake | Manual |  |
| 7 | Suspension System |  |  |
|  | Front | Coil Type |  |
|  | Rear | Leaf |  |
| 8 | ## Tires and Wheel size | To be mentioned |  |
| 9 | Battery Volt | 12 Volts |  |
| 10 | Built in equipment & Accessories | As per Specification |  |
| 11 | Type of AC included | Auto Air-Conditioned (Front-Rear) (Built-in) |  |
| 12 | Repair tools | To be mentioned |  |

| 13 | Spares | To be mentioned |  |
| --- | --- | --- | --- |
| 14 | List of Standard Tools | To be mentioned |  |
| 15 | List of Accessories | To be mentioned |  |
| 16. | Black Smoke Emission | 65 HSU |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars (GTP) of Electric Vehicle

| Sl. No. | Description | Purchaser's Requirement | Manufacturer's Guaranteed Data |
| --- | --- | --- | --- |
| 1 | General |  |  |
|  | a) Country of Origin | To be mentioned |  |
|  | b) Country of make | To be mentioned |  |
|  | c) Name of Manufacturer | To be mentioned |  |
|  | d) Year of manufacture | 2024 or latest |  |
|  | e) Model | To be mentioned |  |
|  | f) Brand | To be mentioned |  |
| 2 | Body |  |  |
|  | a) Overall length | To be mentioned |  |
|  | b) Overall width | To be mentioned |  |
|  | c) Overall height | To be mentioned |  |
|  | d) Wheel track- front/rear (mm) | To be mentioned |  |
|  | e) Wheel base | To be mentioned |  |
|  | f) Ground clearance | To be mentioned |  |
|  | g) Gross Vehicle weight, kg | To be mentioned |  |
|  | h) Number of doors | 4(four) |  |
|  | i) Seating Capacity | 5 Seated |  |
|  | j) Loading Capacity, kg (Min/Max) | To be mentioned |  |
|  | k) Color | Manufacturer’s standard |  |
|  | l) Drive | Right hand drive (RHD) |  |
| 3 | Electric Motor |  |  |
|  | a) Model | To be mentioned |  |
|  | b) Type | Permanent magnet synchronous motor |  |
|  | c) Power, kW | 100 (Minimum) |  |
|  | d) Torque, N.m. | 300 (Minimum) |  |
| 4 | Performance |  |  |
|  | a) Acceleration 0-100 km/h, s | 11 (Maximum) |  |
|  | b) Driving range: WLTP-Combined, km | 340 (Minimum) |  |
| 5 | Battery |  |  |
|  | a) Battery type | Blade Battery |  |
|  | b) Battery Capacity, kWh | 49.50 (Minimum) |  |
| 6 | Brake |  |  |
|  | a) Front Brake | Ventilated Disc |  |
|  | b) Rear Brake | Disc |  |
| 7 | Suspension System |  |  |
|  | Front Suspension | Macpherson strut |  |
|  | Rear Suspension | Multi-link |  |
| 8 | ## Tyre |  |  |
|  | ## Wheel Type | Alloy |  |
|  | ## Tyre Size | 215/60 R17 (Minimum) |  |
| 9 | Built in equipment & Accessories | As per Specification |  |
| 10 | Type of AC included | Automatic Air-Conditioning (Front-Rear) (Built-in) |  |
| 11 | Repair tools | To be mentioned |  |

| 12 | Spares | To be mentioned |  |
| --- | --- | --- | --- |
| 13 | List of Standard Tools | To be mentioned |  |
| 14 | List of Accessories | To be mentioned |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for Single-Core, 35 mm2 PVC Insulated and PVC Sheathed Copper Cable

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | 1CX35 sq. mm PVC Insulated and PVC Sheathed Cables |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
| 5 | Cable Size | mm2 | 1CX35 |  |
| 6 | Material |  | PVC Insulated and PVC Sheathed plain annealed copper. |  |
| 7 | Numbers & Diameter of wires | mm | 19/1.53 |  |
| 8 | Maximum resistance at 20 deg. C | /KM | 0.524 |  |
| 9 | Nominal thickness of insulation | mm | 1.2 |  |
| 10 | Nominal thickness of sheath | mm | 1.8 |  |
| 11 | Colour of sheath |  | Black |  |
| 12 | Approximate outer diameter | mm | 13.9 |  |
| 13 | Approximate weight | Kg/KM | 482 |  |
| 14 | Continuous permissible service voltage | V | 600/1000 |  |
| 15 | Current rating at 30 deg. C ambient temperature U/G | Amps | 155 |  |
| 16 | Current rating at 35 deg. C ambient in air | Amps | 160 |  |
| 17 | Drum wound length | M | 500 |  |
| 18 | Net Weight | Kg | Shall be mentioned |  |
| 19 | Gross weight | Kg | Shall be mentioned |  |
| 20 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |
| 21. | Manufacturer must comply all the features of mentioned in Technical Specification (Section 7) |  | Yes |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for Single-Core, 25 mm2 PVC Insulated and PVC Sheathed Copper Cable

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | 1CX25 sq. mm PVC Insulated and PVC Sheathed Cables |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
| 5 | Cable Size | mm2 | 1CX25 |  |
| 6 | Material |  | PVC Insulated and PVC Sheathed plain annealed copper. |  |
| 7 | Numbers & Diameter of wires | mm | 7/2.14 |  |
| 8 | Maximum resistance at 30 deg. C | /KM | 0.727 |  |
| 9 | Nominal thickness of insulation | mm | 1.2 |  |
| 10 | Nominal thickness of sheath | mm | 1.8 |  |
| 11 | Colour of sheath |  | Black |  |
| 12 | Approximate outer diameter | mm | 12.4 |  |
| 13 | Approximate weight | Kg/KM | 363 |  |
| 14 | Continuous permissible service voltage | V | 600/1000 |  |
| 15 | Current rating at 30 deg. C ambient temperature U/G | Amps | 130 |  |
| 16 | Current rating at 35 deg. C ambient in air | Amps | 125 |  |
| 17 | Drum wound length | M | 500 |  |
| 18 | Net Weight | Kg | Shall be mentioned |  |
| 19 | Gross weight | Kg | Shall be mentioned |  |
| 20 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for PVC Insulated Quadruplex Copper Cable (4⨯16rm)

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | PVC Insulated Self Supported Quadruplex Copper Cable (4⨯16rm) |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
| 5 | Installation |  | Outdoor overhead, high humid, rainfall and temperature |  |
| 6 | Type |  | Self-supported, weather proof PVC insulated |  |
| 7 | Continuous permissible service voltage | V | 600/1000 |  |
| 8 | Cable Size | mm2 | 3x16rm+16rm |  |
| 9 | Number of Core |  | 4 Single Core (3 Phase + 1 Neutral) |  |
| 10 | Cable Construction |  | Each single core cable spirally arranges to form a self-supporting assembly without any cover |  |
| 11 | Twisted Assemblies | mm | 25 to 45 times the diameter of one of the insulated conductors |  |
| 12 | Pitch length | mm | Shall be mentioned |  |
| 13 | Conductor Material |  |  |  |
|  | a) Phase Conductor |  | Plain annealed copper conductor |  |
|  | b) Neutral Conductor |  | Hard drawn copper conductor |  |
| 14 | Insulation Material |  | High quality electric grade weather proof PVC over core for water tightness but ensuring case of stripping |  |
| 15 | Colour |  |  |  |
|  | a) Phase Conductor |  | Black |  |
|  | b) Neutral Conductor |  | Green |  |
| 16 | Thickness of insulation | mm | 1.6 (Minimum) |  |
| 17 | Sheath |  | None |  |
| 18 | Numbers & Diameter of wires | mm | 7/1.71 |  |
| 19 | Cross Sectional area of Cond. (Phase & Neutral) | Sq. mm | 16 |  |
| 20 | Maximum dc resistance at 20 deg. C | /KM | 1.15 |  |
| 21 | Overall Diameter of Conductor |  |  |  |
|  | a) Phase Conductor | mm | Shall be mentioned |  |
|  | b) Neutral Conductor | mm | Shall be mentioned |  |
| 22 | Weight of Conductor | Kg/KM | ≥ 765 |  |
| 23 | Continuous Current rating at 35 deg. C ambient in air | Amps | ≥ 75 |  |
| 24 | Maximum allowable tension | Kg | Shall be mentioned |  |
| 25 | Minimum Breaking Load of Conductor |  |  |  |
|  | a) Phase Conductor | Kg | Shall be mentioned |  |
|  | b) Neutral Conductor | Kg | Shall be mentioned |  |
| 26 | Net Weight of conductor in a drum/Reel | Kg | Shall be mentioned |  |
| 27 | Gross weight of Drum/Reel including conductor | Kg | Shall be mentioned |  |
| 28 | Drum wound length | M | 500 |  |
| 29 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for PVC Insulated Quadruplex Copper Cable (4⨯6rm)

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | PVC Insulated Self Supported Quadruplex Copper Cable (4⨯6rm) |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
| 5 | Installation |  | Outdoor overhead, high humid, rainfall and temperature |  |
| 6 | Type |  | Self-supported, weather proof PVC insulated |  |
| 7 | Continuous permissible service voltage | V | 600/1000 |  |
| 8 | Cable Size | mm2 | 3x6rm+6rm |  |
| 9 | Number of Core |  | 4 Single Core (3 Phase + 1 Neutral) |  |
| 10 | Cable Construction |  | Each single core cable spirally arranges to form a self-supporting assembly without any cover |  |
| 11 | Twisted Assemblies | mm | 25 to 45 times the diameter of one of the insulated conductors |  |
| 12 | Pitch length | mm | Shall be mentioned |  |
| 13 | Conductor Material |  |  |  |
|  | a) Phase Conductor |  | Plain annealed copper conductor |  |
|  | b) Neutral Conductor |  | Hard drawn copper conductor |  |
| 14 | Insulation Material |  | High quality electric grade weather proof PVC over core for water tightness but ensuring case of stripping |  |
| 15 | Colour |  |  |  |
|  | a) Phase Conductor |  | Black |  |
|  | b) Neutral Conductor |  | Green |  |
| 16 | Thickness of insulation | mm | 1.6 (Minimum) |  |
| 17 | Sheath |  | None |  |
| 18 | Numbers & Diameter of wires | mm | 7/1.05 |  |
| 19 | Cross Sectional area of Cond. (Phase & Neutral) | Sq. mm | 6 |  |
| 20 | Maximum dc resistance at 20 deg. C | /KM | 3.030 |  |
| 21 | Overall Diameter of Conductor |  |  |  |
|  | a) Phase Conductor | mm | Shall be mentioned |  |
|  | b) Neutral Conductor | mm | Shall be mentioned |  |
| 22 | Weight of Conductor | Kg/KM | ≥ 370 |  |
| 23 | Current rating at 35 deg. C ambient in air | Amps | ≥ 41 |  |
| 24 | Maximum allowable tension | Kg | Shall be mentioned |  |
| 25 | Minimum Breaking Load of Conductor |  |  |  |
|  | a) Phase Conductor | Kg | Shall be mentioned |  |
|  | b) Neutral Conductor | Kg | Shall be mentioned |  |
| 26 | Net Weight of Conductor in a Drum/Reel | Kg | Shall be mentioned |  |
| 27 | Gross weight of Drum/Reel including Conductor | Kg | Shall be mentioned |  |
| 28 | Drum wound length | M | 1000 |  |
| 29 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars for PVC Insulated Duplex Copper Cable (4rm)

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item |  | PVC Insulated & Twisted Duplex Copper Cable |  |
| 2 | Name of the Manufacturer |  | Shall be mentioned |  |
| 3 | Address of the Manufacturer |  | Shall be mentioned |  |
| 4 | Standard |  | Performance Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
| 5 | Installation |  | Outdoor overhead, high humid, rainfall and temperature |  |
| 6 | Type |  | Self-supported, weather proof PVC insulated |  |
| 7 | Cable Size | mm2 | 4rmX4rm |  |
| 8 | Number of Core |  | 2 Single Core (1 Phase + 1 Neutral) |  |
| 9 | Cable Construction |  | Each single core cable spirally arranges to form a self-supporting assembly without any cover |  |
| 10 | Twisted Assemblies | mm | 25 to 45 times the diameter of one of the insulated conductors |  |
| 11 | Pitch length | mm | Shall be mentioned |  |
| 12 | Conductor Material |  |  |  |
|  | a) Phase Conductor |  | Plain annealed copper conductor |  |
|  | b) Neutral Conductor |  | Hard drawn copper conductor |  |
| 13 | Insulation Material |  | High quality electric grade weather proof PVC over core for water tightness but ensuring case of stripping |  |
| 14 | Colour |  |  |  |
|  | a) Phase Conductor |  | Black |  |
|  | b) Neutral Conductor |  | Green |  |
| 15 | Thickness of insulation | mm | 1.6 (Minimum) |  |
| 16 | Numbers & Diameter of wires | mm | 7/0.85 |  |
| 17 | Maximum resistance at 20 deg. C | /KM | 4.61 |  |
| 18 | Overall Diameter of Conductor |  |  |  |
|  | a) Phase Conductor | mm | Shall be mentioned |  |
|  | b) Neutral Conductor | mm | Shall be mentioned |  |
| 19 | Approximate weight | Kg/KM | 140 |  |
| 20 | Continuous permissible service voltage | V | 600/1000 |  |
| 21 | Current rating at 35 deg. C ambient in air | Amps | 35 |  |
| 22 | Drum wound length | M | 1000 |  |
| 23 | Maximum allowable tension | Kg | Shall be mentioned |  |
| 24 | Minimum Breaking Load of Conductor |  |  |  |
|  | a) Phase Conductor | Kg | Shall be mentioned |  |
|  | b) Neutral Conductor | Kg | Shall be mentioned |  |
| 25 | Net Weight | Kg | Shall be mentioned |  |
| 26 | Gross weight | Kg | Shall be mentioned |  |
| 27 | Treated Wooden Drum Standard |  | AWPA C1 – 82, C2 –83, C16 –82, P5 –83. |  |

| Seal and Signature of the manufacturer: | Seal and Signature of the Bidder: |
| --- | --- |

- Guaranteed Technical Particulars of 11kV, XLPE, 3C x 70mm2 COPPER CABLE

| Sl. No. | Description | Unit | Purchaser’s Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- | --- |
| 1 | Name of the Item | - | 3C x70mm2 11 kV XLPE Insulated Copper Cables |  |
| 2 | Manufacturer’s name & address With website, official domain email. | - | To be mentioned |  |
| 3 | Year of Manufacturing | Yr. | Not before 2025 |  |
| 4 | Standard | - | Performance, Design and Testing shall be in accordance to the BS, IEC, BDS or equivalent International standards. |  |
|  | Country of Origin | - | To be mentioned |  |
| 5. | VOLTAGE Voltage between phases of three Phase circuit U Umax | kV kV | 11 12 |  |
| 6. | CORES Number of Cores | No. | Three |  |
| 7. | Manufacturing Process |  | To be mentioned |  |
| 8. | CONDUCTOR material cross sectional area Min. No. & Dia of wires | mm2 Nos./mm | Electrolytic annealed copper 70 19/ To be mentioned |  |
| 9. | CONDUCTOR SCREEN Material Nominal Thickness Diameter over screen | mm mm | semi-conducting XLPE 0.8 To be mentioned |  |
| 10. | INSULATION Material Type of dry curing Nominal Thickness Diameter of over Insulation | mm mm | XLPE Inert gas 3.4 To be mentioned |  |
| 11. | CORE SCREEN Material Nominal Thickness Diameter over screen | mm mm | semi-conducting XLPE 0.8 To be mentioned |  |
| 12. | METALLIC SCREEN Number and diameter of copper screen strands or Copper Wire with helically applied Copper Tape | No./mm or No./mm with Thickness of tape | Based on Design Calculation |  |
| 13. | INNER JACKET Material Nominal Thickness External diameter | mm mm | Extruded PVC (ST-2) 1.4 To be mentioned |  |
| 14. | ARMOUR Number & diameter of amour wire or Thickness of Corrugated Aluminium csheath | No./mm or mm | 38/ To be mentioned |  |
| 15. | OUTER COVERING Material Minimum average thickness | mm | Black extruded MDPE 2.6 |  |
| 16. | COMPLETED CABLE Overall diameter Weight per metre Maximum drum length | mm kg m | 57 5.58 500 |  |
| 17. | CABLE DRUMS Material Overall diameter Width Gross weight (with cable) | mm m kg | Steel To be mentioned To be mentioned To be mentioned |  |
| 18. | CONTINUOUS CURRENT CARRYING CAPACITY Based on the conditions specified: In Air One circuit at 30°C In Ground One circuit at 30°C | A A | 253 220 |  |
| 19. | PERMISSIBLE OVERLOAD In Service Conditions For a period of | % Hours | To be mentioned To be mentioned |  |
| 20. | MAXIMUM CONDUCTOR TEMPERATURE Laid direct in ground Drawn into ducts Erected in air | C C C | 90 90 90 |  |
| 21. | CONDUCTOR SHORT CIRCUIT CURRENT Carrying capacity for one second, Cable load as above prior to Short circuit and final conductor Temperature of 250C` | KA | 10.01 |  |
| 22. | METALIC SCREEN EARTH FAULT CURRENT Carrying capacity for one second, Cable loaded as above prior to Earth fault | KA | 10 (with detail calculation) |  |
| 23. | MINIMUM RADIUS OF BEND Around which cable can be laid | m | 20 times of overall diameter of cable |  |
| 24. | MAXIMUM DC RESISTANCE Per km of cable at 20C of conductor of metallic layer | ohm ohm | 0.2680 To be mentioned |  |
| 25. | MAXIMUM AC RESISTANCE Of conductor per km of cable at Maximum conductor temperature | ohm | 0.348 |  |
| 26. | INSULATION RESISTANCE Per km of cable per core at 20C at maximum rated temperature | Megohm Megohm | 400 40 |  |
| 27. | MAXIMUM ELECTROSTATIC CAPACITANCE Per Km of cable | µF | 0.290 |  |
| 28. | MAXIMUM INDUCED VOLTAGE On metallic layer/sheath Under fault condition | V | To be mentioned |  |
| 29. | MAXIMUM CHARGING CURRENT Per core per metre of cable at Nominal voltage Uo | mA | To be mentioned |  |
| 30. | Working Inductance | mH/km | 0.34 |  |
| 31. | MAXIMUM PULLING TENSION | kg | To be mentioned |  |
| 32. | Manufacturer must comply all the features of Technical Specification (Section 7) | - | Yes |  |

Seal & Signature of the Manufacturer                        Seal & Signature of the Bidder

- Manufacturer’s Guaranteed Technical Data Schedule For Of 230 Volt, 10(60) A, Single Phase Digital Energy Meter

| Sl. No. |  |  | Description | Unit |  | Purchaser's Requirement |  | Manufacturers Particulars |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  | Manufacture's Name and Country | - |  | To be mentioned |  |  |  |
| 2 |  |  | Manufacture's Meter Type/Model | - |  | To be mentioned |  |  |  |
| 3 |  |  | Type | - |  | Electronic |  |  |  |
| 4 |  |  | Connection | - |  | Single phase, two-wire whole current(Unidirectional) |  |  |  |
| 5 |  |  | Rated voltage | volt |  | 230 |  |  |  |
| 6 |  |  | Rated current - Basic current - Maximum current | Amp |  | 10 60 |  |  |  |
| 7 |  |  | Accuracy class | Class |  | 1.0 |  |  |  |
| 8 |  |  | KWh register type | - |  | LCD Display |  |  |  |
| 9 |  |  | Number of digits (Integral + decimal) | Nos. |  | 5+1 |  |  |  |
| 10 |  |  | Meter constant | Impulse/KWh |  | To be mentioned |  |  |  |
| 11 |  |  | Voltage circuit loss at rated voltage | VA &W |  | 10 & 2.0 |  |  |  |
| 12 |  |  | Current circuit loss at rated current | VA |  | 4 |  |  |  |
| 13 |  |  | Impulse withstand voltage | KV |  | 6 |  |  |  |
| 14 |  |  | Starting current (minimum) | MA |  | 0.4% of basic current |  |  |  |
| 15 |  |  | Size of display (minimum) | W χ H |  | 4 χ 8 mm |  |  |  |
| 16 |  |  | Service life (Minimum) | Year |  | 15 (Fifteen) |  |  |  |
| 17 |  |  | Weight of meter | kg |  | To be mentioned |  |  |  |
| 18 |  |  | Overall dimensions (height, width, depth) | mm |  | To be mentioned |  |  |  |
| 19 |  |  | Terminal hole diameter | mm |  | 16 mm. |  |  |  |
| 20 |  |  | Reference standard | - |  | To be mentioned |  |  |  |
| 21 | Type of Battery |  |  | - |  | Lithium |  |  |  |
| 22 | Battery Reserve & Life |  |  | - |  | 10 Years |  |  |  |
| 23 | Built in clock |  |  | - |  | To be mentioned |  |  |  |
| 24 | Rated frequency |  |  | Hz |  | 50 |  |  |  |
| 25 | Place of manufacture/year of manufacture |  |  | - |  | To be mentioned |  |  |  |
| 26 | Variation of voltage |  |  | % |  | ±30% |  |  |  |
| 27 | Variation of Power factor |  |  |  |  | 0.5 lag to 0.8 lead |  |  |  |
| 28 | Terminal |  |  | - |  | Minimum 4 (four) terminal to accommodate 16 sq. mm. size of cable |  |  |  |
| 29 | Warranty(Minimum) |  |  | Years |  | 3 Years |  |  |  |
| 30 | Any other facility (if any) |  |  | - |  | To be mentioned |  |  |  |
| 31 | Valid calibration certificate of the KWH sub-standard meter |  |  |  |  | To be mentioned |  |  |  |

Seal & Signature of the manufacturer:	Seal & Signature of the bidder:

- Manufacturer’s Guaranteed Technical Data Schedule For 110v, 3x5(6)A, 3-Phase, 4-Wire Accuracy Class 0.2s Solid State Double Tariff Programmable Energy Meter.

| Sl. No. | Name of Items |  |  | Unit | Purchaser's Requirement | Full Technical Specification & Standard (to be mentioned) |
| --- | --- | --- | --- | --- | --- | --- |
| 01 | Reference standard |  |  |  | Relevant IEC standard |  |
| 02 | Manufacturer’s Name and address |  |  |  | To be mentioned |  |
| 03 | Meter’s Type & Model |  |  |  | To be mentioned |  |
| 04 | Country of origin |  |  |  | To be mentioned |  |
| 05 | Country of Manufacture |  |  |  | To be mentioned |  |
| 06 | Year of manufacture |  |  |  | To be mentioned |  |
| 07 | Connection |  |  |  | 3-phase, 4-wire solidly grounded neutral |  |
| 08 | Number of element |  |  | Nos. | 03 (three) |  |
| 09 | Rated voltage (P-P) |  |  | Volt | 110V |  |
| 10 | Minimum Biasing Voltage (P-P) |  |  | Volt | 40V |  |
| 11 | Rated current |  |  |  |  |  |
|  | I) Basic current (Ib) |  |  | Amp | 5 A |  |
|  | II) Maximum current (Imax) |  |  | Amp | 6 A |  |
| 12 | Frequency |  |  | Hz | 50 |  |
| 13 | Variation of frequency |  |  | % | ±2.5 |  |
| 14 | Variation of voltage |  |  | % | -20% to +10% |  |
| 15 | Accuracy class |  |  |  | 0.2 (point two)S |  |
| 16 | Register type |  |  |  | LCD display |  |
| 17 | Number of digit (integer with decimal) |  |  | Nos. | 5 with 3 (programmable) |  |
| 18 | Starting current |  |  | Amp | 0.1% of Basic Current (Ib) |  |
| 19 | Losses at nominal load |  |  | Watt & VA | To be mentioned |  |
| 20 | Meter constant |  |  | Imp./KWh | To be mentioned |  |
| 21 | Integration period |  |  |  | 30 (thirty) minutes |  |
| 22 | Resetting period |  |  |  | 1 (one) month |  |
| 23 | Cumulative MD transfer cycle timing device |  |  |  | Built-in |  |
| 24 | Size of the digit of display |  |  | (W x H) in mm | 4 X 8 |  |
| 25 | No. of terminal |  |  | Nos. | 10 (min) |  |
| 26 | Diameter of Terminal & Bore |  |  | Mm | To accommodate 6 Sq. mm size of cable. |  |
| 27 | Battery service life and Shelf life (minimum) |  |  | Year | 15 (fifteen) |  |
| 28 | Type of Battery |  |  |  | Lithium-ion Battery (non-rechargeable). |  |
|  | Country of origin |  |  |  | To be mentioned |  |
|  | Voltage |  |  | V | Upto 6 Volt |  |
|  | Capacity |  |  | mAh | min1400-1700 mAh |  |
|  | Lifetime |  |  | yrs | Min 10(ten)yrs |  |
| 29 | Clock |  |  |  | Built in Real Time Clock(RTC) as per IEC |  |
| 30 | Warranty |  |  | Year | 3(three) |  |
| 31 | Meter Service life (minimum) |  |  | Year | 15 (fifteen) |  |
| 32 | Weight of meter |  |  | Kg | To be mentioned |  |
| 33 | Dimensions |  |  | mm x mm x mm | To be furnished |  |
| 34 | Outlines, drawings & catalogue |  |  |  | To be mentioned |  |
| 35 | Performance curve for balanced & unbalanced load |  |  |  | To be mentioned |  |
| 36 | Meter Body sealing condition |  |  |  | Hermetically sealed/ Ultrasonic welded with mechanically interlocked. ( means break to open) |  |
| 37 | Meter parameter configuration |  |  |  | To be configured: Both software and hardware lock as per sub-clause 7.01.03.02 |  |
| 38 | Country of manufacture |  |  |  | To be mentioned |  |
| 39 | Place of testing |  |  |  | To be mentioned |  |
| 40 | Losses at nominal load |  |  | Watt & VA | To be mentioned |  |
| 41 | Voltage Circuit Loss at rated voltage |  |  | Watt & VA | To be mentioned |  |
| 42 | Current Circuit Loss at rated current |  |  | VA | To be mentioned |  |
| 43 | Communication |  |  |  | Plug & Play 4G Communication module |  |
| 44 | Application Protocol |  |  |  | DLMS/COSEM |  |
| 45 | Memory storage |  |  |  | Shall be mentioned by putting Yes / No |  |
|  | I) |  | Equipment Identification code. |  |  |  |
|  | II) |  | Security code |  |  |  |
|  | III) |  | Access code |  |  |  |
|  | IV) |  | Number of power interruption with date & time |  |  |  |
|  | V) |  | Latest power failure time & date |  |  |  |
|  | VI) |  | Event logs. |  |  |  |
|  | VII) |  | Cumulative KWh (Total, Peak & Off-peak) |  |  |  |
|  |  |  | KVarh (Q1+Q4) |  |  |  |
|  | VIII) Load Profile with 30 min interval at least 365 days for: |  |  |  |  |  |
|  |  | - KWh, kVarh (Q1+Q4) |  |  |  |  |
|  |  | - Phase Voltage |  |  |  |  |
|  |  | - Phase Amps |  |  |  |  |
|  |  | - Power Factor (PF) |  |  |  |  |
| 46 | List of recommended spare parts (If any) |  |  |  | To be mentioned |  |
| 47 | All other technical particulars which is mentioned in section-07. |  |  | Yes/No | Yes |  |
| 48 | Manufacturer must comply all the features of Technical Specification ( Section 7) |  |  |  | Yes |  |

Seal & Signature of the manufacturer:	Seal & Signature of the bidder:

- Manufacturer’s Guaranteed Technical Data Schedule For 400v,  3x10(60) A, 3-Phase, 4-Wire Solid State Double Tariff Fully Programmable Energy Meter

| Sl. No. | Name of Items |  | Unit | Purchaser's Requirement | Full Technical Specification & Standard (to be mentioned) |
| --- | --- | --- | --- | --- | --- |
| 01 | Reference Standard |  |  | Relevant ANSI /IEC standard |  |
| 02 | Manufacturer’s Name & Address |  |  | To be mentioned |  |
| 03 | Manufacturer’s Type & Model |  |  | To be mentioned |  |
| 04 | Construction / Connection |  |  | 3-phase, 4-wire solidly grounded neutral |  |
| 05 | Installation |  |  | Indoor/ Outdoor Installation |  |
| 06 | Number of element |  | Nos. | 3 (three) |  |
| 07 | Rated voltage(P-P) |  | Volt | 400V |  |
| 08 | Minimum Biasing Voltage (P-P-N) |  | Volt | 80V |  |
| 09 | Variation of Frequency |  | % | ±2 |  |
| 10 | Variation of Voltage |  | % | +10, -20 |  |
| 11 | Accuracy Class |  |  | 1.0 (One) |  |
| 12 | Rated Current I) Nominal (Base) Current (Ib) II) Maximum Current (Im) |  | Amp Amp | 10 A 60 A |  |
| 13 | Register Type |  |  | LCD display |  |
| 14 | Number of digit (integer with decimal) |  | Nos. | 6 integer with 1 decimal |  |
| 15 | Starting current |  | Amp | 0.4% of Nominal Current |  |
| 16 | Losses at nominal load |  | Watt & VA | To be mentioned |  |
| 17 | Meter constant |  | Imp./Kwh | To be mentioned |  |
| 18 | Integration period Resetting period Cumulative MD transfer cycle timing device |  | Minutes Months | 30 (thirty) minutes 1 (one) month Built-in Built-in |  |
| 19 | Size of the digit of display |  | (W x H) in mm | 4 X 8 |  |
| 20 | No. of Terminal |  | Nos. | 8 (min.) |  |
| 21 | Type of Socket and Country of Origin |  |  | To be mentioned |  |
| 22 | Battery service life and Shelf life (minimum) |  | Year | 15 (fifteen) |  |
| 23 | Year of manufacture |  |  | To be mentioned |  |
| 24 | List of recommended spare parts (If any) |  |  | To be mentioned |  |
| 25 | Warranty |  | Year | 3(three) |  |
| 26 | Meter Service life (minimum) |  | Year | 15 (fifteen) |  |
| 27 | Weight of meter |  | Kg | To be mentioned |  |
| 28 | Dimensions |  | mm x mm x mm | To be mentioned |  |
| 29 | Outlines, drawings & leaflets |  |  | To be mentioned |  |
| 30 | Performance curve for balanced & unbalanced load |  |  | To be mentioned |  |
| 31 | Meter Sealing Condition |  |  | Hermetically sealed/ Ultrasonic welded/ mechanicaly interlocked. Hermetically sealed means break to open |  |
| 32 | a) Country of Origin b) Place of Manufacture c) Place of Testing |  |  | To be mentioned |  |
| 33 | Memory storage : |  |  | Shall be mentioned by putting Yes / No |  |
|  | I) | Equipment identification Code. |  |  |  |
|  | II) | Security code |  |  |  |
|  | III) | Access code |  |  |  |
|  | IV) | Number of power interruption with date & time |  |  |  |
|  | V) | Latest power failure Time & Date |  |  |  |
|  | VI) | Event logs( Terminal Cover open, Body cover open etc.) |  |  |  |
|  | VII) | Cumulative KWh (Peak, Off-Peak, Total), Cumulative Total KVarh (Q1+Q4), Cumu. MD reading etc, |  |  |  |
|  | VIII) Load Profile with 30 min interval at least 180 days for: |  |  |  |  |
|  | - KWh, kVarh (Q1+Q4) |  |  |  |  |
|  | - Phase Voltage - Phase Amps - MD With Date & Time. |  |  |  |  |
| 34 | All other technical particulars which is mentioned in section-07. |  |  |  |  |

The Tenderer should complete all the columns as required]

| Signature: Name & Designation of tenderer | Signature Name and Designation of Manufacturer |
| --- | --- |

The Tenderer shall fill up all the Guaranteed Technical Particulars in accordance with the purchaser’s requirements

| Signature: | [insert signature of authorised representative of the Tenderer] |
| --- | --- |
| Name: | [insert full name of signatory with National ID] |
| In the capacity of: | [insert designation of signatory] |
| Duly authorised to sign the Tender for and on behalf of the Tenderer |  |