BANGLADESH POWER DEVELOPMENT BOARD

BIDDING DOCUMENT

For

Electrification at Bhashanchar of Noakhali District

(Single Stage Two Envelope Bidding Process)

Bidding Document

(Volume 2 of 3 of the Bidding Document)

Invitation for Tender No: 27.11.0000.101.14.079.25-2337,  Dated: 14/09/2025

Secretary

Bangladesh Power Development Board

Wapda Building (1st Floor), Motijheel, C/A.

Dhaka, Bangladesh

SEPTEMBER, 2025

Part 2: Section VII:  Employer’s Requirements

Contents

1. Scope of Supply of Plant and Installation Services by the Contractor	5

2.	Specification	8

2.1	Introduction	8

2.2	OFF GRID PV-BESS-DG POWER plant design concept	10

The entire plant should be designed to function at its desired and guaranteed functional performance level with expected working/functional life considering the climatic conditions prevailing at the site. The corrosion protection level should be in consideration of the climatic condition for all the components and subsystems.	10

2.2.1 Plant Overview	11

2.2.2 Electrical Voltage Level	12

2.3	CONTRACTOR’S AND EMPLOYER’S OBLIGATION	12

2.3.1 Employer’s Basic Obligations	12

2.3.2 Contractor’s Basic Obligations	13

2.4	GENERAL REQUIREMENTS	13

2.5	FUNCTIONAL REQUIREMENTS	14

2.5.1 Site Preparation	14

2.5.2 Metrological Stations	15

2.5.3 Perimeter Wall	16

2.5.4 Drainage System	16

2.5.5 Roads and Pathways	16

2.5.6 Mounting Structures	17

2.5.7 Inter-Row Spacing for PV Mounting Structures	17

2.5.8 Lightning Protection System	17

2.5.9 External Lighting System	17

2.5.10 Earthing System	18

2.5.11 Water Supply and Septic System	19

2.5.12 Fire Fighting and Detection System	19

2.5.13 Plant Layout	19

2.5.14 Electrical Lines	20

2.6	RESOURCE ASSESSMENT	20

2.7	PLANT PERFORMANCE ASSESSMENT	20

2.7.2 BESS Guarantee Performance Test	20

2.7.3 Start-Up of The Plant	20

2.7.4 Performance Test	21

2.8	FUNCTIONAL WARRANTIES	23

2.8.1 Defects Warranty	24

2.8.2 Project Components Warranty	24

2.8.3 Production Warranty	24

2.9	OPERATION AND MAINTENANCE	24

2.9.1 PV Module Cleaning	24

2.9.2 Training	25

2.10	WATER SUPPLY, WATER DRAINAGE AND WATER TREATMENT SYSTEMS	25

2.10.1 Water quality requirements and water flow	25

2.10.2 Drinking water supply	25

2.10.3 Firefighting water supply	25

2.10.4 Water drainage system	25

2.10.5 Office/Administrative Building sewage system	26

2.10.6 Rainwater drainage	26

2.11	Technical Specification	26

2.11.1 Solar Photovoltaic (PV) Module	27

2.11.2 Module Mounting Structure	33

2.11.3 Grid Tied Inverter (Local Grid)	35

2.11.4 Battery Inverter (Smart Inverter) (Usually Named A “Pcs” In A Bess System)	39

2.11.5 Battery Energy Storage System and Battery Management And Pcs	44

2.11.6 Power Transformer	48

2.11.8 LV/MV CABLE AND ACCESSORIES	74

2.11.8.1 MV Cable and Accessories	74

2.11.8.2 LV Cable and Accessories	77

2.11.9 Plant Control and Monitoring System	79

2.11.10 DC, UPS & Auxiliary Power Supply	88

2.11.11	Protection and Control System	91

2.11.12 Static Var Generator	92

2.11.13 Fire Fighting System	93

Security and Surveillance	94

2.11.15 Emergency Diesel Generator	95

2.11.16 Weather Station/ Meteorological Measurement Station	95

2.11.17 Distribution System	97

1.04 Design, Supply, Erection, Installation, Testing and Commissioning of 11kV, 11/0.4kV and 0.4kV Overhead Distribution Lines:	99

18.0 Technical Specifications/Requirements of 11/0.415KV, 250KVA; 100KVA & 50KVA 3-Phase Distribution Transformer	129

Standards	129

Specifications	129

Major Components	129

FEATURES AND ACCESSORIES	130

INFORMATION REQUIRED	131

TEST REPORTS	131

Transformer Construction	132

Scope	135

General	135

Ratings	135

Design:	136

TESTS	138

SPARE PARTS:	138

INFORMATION REQUIRED	138

TEST REPORTS	139

PACKAGING:	139

OTHER STANDARDS:	139

TRANSFORMER	139

BIBLIOGRAPHY OF REFERENCE STANDARDS, (revision from 2010 to the latest revision)	140

21.0 TECHNICAL DESCRIPTION OF 11 KV DROP OUT FUSE CUT OUT (DOFC)	142

RATINGS	142

DESIGN	142

Fuse Support Assembly	143

Fuse Holder Assembly	143

Mounting Bracket	143

Lock Washers	143

TEST REPORTS:	143

a.	Type Test:	144

b.	Special Test:	144

3	147

Construction	147

Specifications:	152

Specifications:	153

2.11.20 CIVIL WORKS	179

Ground Floor	198

First Floor	199

Second Floor – Administrative Purpose	199

Third Floor – Emergency Support Service (Accommodation)	199

Furniture and Fixtures	199

3.	Test Requirements and Acceptance Criteria	202

3.1	CODES AND STANDARDS	203

3.2	WORK PROGRESS INSPECTION	203

3.3	TEST EQUIPMENT	203

3.4	FACILITIES FOR TESTING AND RELATED	204

3.5	REJECTION DUE TO TEST RESULTS	204

3.6	FORMAL REQUIREMENT FOR INSPECTION AND TESTING	204

3.6.1 Inspection and Testing Program	204

3.6.2 Construction Progress Inspections and Certifications	206

3.6.3 Staffing	206

3.6.4 Test Procedures and Testing Program	207

3.6.5 Commissioning	207

3.6.6 Commissioning Tests	208

4.	QUALITY aSSURANCE pLAN	210

4.1	CONTRACTOR DUTIES	210

4.2	QUALITY PROGRAMS, PLANS AND PROCEDURES	211

4.2.1 Project Quality Plan	211

4.2.2 Individual Quality Plans	211

4.2.3 Ready for Implementation	211

4.2.4 Control Procedures	211

4.2.5 Inspection and Test Plans	211

4.3	SPECIFIC REQUIREMENTS	212

4.3.1 Quality Audit	212

4.3.2 Design Control	212

4.3.3 Inspection and Testing	212

4.3.4 Quality Documentation	213

4.3.5 Criticality	213

4.4	Quality Plan Contents	213

4.5	Purchased Material and Equipment	214

4.6	Company Criticality Rating System for Procured Materials and Equipment	215

4.7	Organizational Responsibilities	216

4.8	Quality Management Coordination Scope	216

5	documentation to be provided by the company	218

5.1	PROJECT DOCUMENTATION	219

5.2	FINAL PROJECT DOCUMENTATION	222

5.3	AS-BUILT DRAWINGS	222

5.4	ACCEPTANCE AND CLOSE UNIT REPORT	222

5.5	OPERATION AND MAINTENACE MANUAL	223

5.6	TRAINING PROGRAM FOR THE EMPLOYER	223

6	technical document to be included in the technical bid envelope	224

6.1	Technical Documentation	224

6.2	List of Preferred Suppliers	226

Annex I : Indicative Single Line Diagram	227

ANNEX III: Guaranteed Annual Performance Schedule	228

ANNEX IV: Third Party Independent Testing Laboratories/ Institutions	229

ANNEX V: Annual Guaranteed Dischargeable Energy & Round-Trip Efficiency	230

ANNEX VI: Guaranteed Components of Distribution System	231

Climate Data	237

Tyre and Wheel	238

Climate Data	240

Tyre and Wheel	241

# 1. Scope of Supply of Plant and Installation Services by the Contractor

The project scope will include, but is not limited to, the following broad areas. More details are provided later in the sections below. This specification mostly defines the functional design and operational requirements. It also provides site specific data and defines the environmental constraints within which the plant must operate. The work stated in this specification shall cover design, engineering, manufacture, supply, testing, packing, forwarding, supply, transportation, unloading, storage, installation and commissioning, civil construction, distribution line construction, battery energy storage installation-commissioning and development of an 8 MW (AC) off-grid PV-BESS-DG Power Plant at Bhashanchar of Noakhali District in Bangladesh on full turnkey basis.

The work shall be carried out in accordance with the conditions of this document, and shall include followings:

- The design, manufacture and supply of off-grid PV-BESS-DG Power Plant Power Plant, integrating BESS and diesel generator and plant control EMS.

- Supply and installation of Battery Energy Storage System (BESS).

- Supply and installation of Diesel Generator (DG).

- Supply and installation of Static Var Generator (SVG).

- Supply and installation of LV/11kV Power Transformers.

- Supply and installation of 0.4/11kV Power Transformer (for DG).

- Supply and installation of 11/0.4kV Auxiliary Transformers.

- Supply and construction of 11 kV Substation including LV and 11 kV Switchgear & Protection System.

- Supply and Construction of 11 kV, 11/0.4 KV, .4 KV Distribution Line.

- Supply and installation of 11/0.4kV, 250KVA, 11/0.4kV, 100 kVA, 11/0.4kV 50kVA, 6.3/0.23kV, 10kVA distribution transformers.

- Supply and Installation of End Mile Connection.

- Supply and installation of DC, UPS & Auxiliary Power Supply.

- Supply and installation of Metering System.

- Supply and Installation of PCMS system.

- Supply and installation of Security & Surveillance System.

- Performance testing of the Complete System.

- Supply of Fire Protection and Fire Detection Facilities.

- Construction of Main Road, Perimeter Road and Internal Road.

- Supply and construction of all civil and building works for the power plant.

- Supply of O&M Vehicle.

- Survey, preparation of drawing, land development, landscaping of the proposed site.

- Taking all necessary arrangements for the transportation of goods to the project site.

[Noteworthy facts: Due to the natural characteristics of Bhashanchar Island, it is not suitable for the transportation of heavy plant equipment throughout the entire year. Therefore, effective time management should be implemented to ensure the timely and efficient transportation of such equipment to complete the project in due time.]

The scope of supply, works and services shall cover, but not limited to the following:

- The assessment of the Site;

- The development, detailed design, engineering (including equipment specifications), permitting, procurement, manufacturing, factory testing, transport to site, erection, construction, commissioning and performance testing of the PV plant, BESS and other new installations;

- Road works that in the view of the Bidder are necessary for the construction and operation of the PV plant the works and services related to preparation, civil, mechanical, electrical, I&C and communication works including all required equipment for the execution of these works and services providing security on site as per insurance requirements and the security technical specifications of the Employer and per all applicable codes and standards;

- The training of personnel according to Employer´s Requirements;

- Environmental protection complying with local standards.

The bidder shall include in its scope all facilities & equipment necessary for the generation of power from the Solar PV plant, distribution of energy to the consumer & store energy in BESS and all works & services including workshop and store equipment, special tools and handling equipment, spare parts, consumables, etc. necessary for complete, safe and reliable operation and preventive and corrective maintenance of the off-grid PV-BESS-DG Power Plant. Furthermore, the bidder shall be responsible for the security at the site during the installation process.

The work shall be performed according to the Good Industry Practice which means, at a particular time, those practices, methods and acts as are in accordance with good standards of prudence applicable to the international electricity generation industry which would have been expected to accomplish the desired result at lowest reasonable cost consistent with reliability, safety and expedition. The scope includes also works not explicitly stated in the Employers Requirements or elsewhere in the tender documents but which are reasonably required for the installation and operation of the off-grid PV-BESS-DG Power Plant according to Good Engineering Practice.

Reputable manufacturers shall manufacture new equipment, which shall be subject to Employer’s review and approval. No used, reconditioned or salvaged equipment or material will be allowed. All equipment used in connection with the Project shall be of proven design for the intended use of the equipment. As a general principle, the latest, commercially proven, most modern and up-to-date technologies will be selected and licensing terms agreed with the objective of maximizing value to the Employer.

The Plant and associated storage & distribution system shall be designed, manufactured, erected and configured in such a way that it will achieve high life expectancy, high availability and reliability. All parts of the Plant shall be suitable in every respect for continuous operation at maximum efficiency as well as part loads and minimum load, under consideration of the climatic conditions peculiar to the site and environmental restrictions. But the Bidder must design the off-grid PV-BESS-DG Power Plant including all required structures and facilities in such a way that they withstand also extreme weather conditions and other disasters according to the latest version of the Bangladesh National Building Code (BNBC). Each off-grid PV-BESS-DG Power Plant element or component shall be designed to withstand the design ambient conditions as stated under the Section VII.

All equipment and systems shall be built according to internationally recognized standards and shall comply with all the applicable national codes and statutory requirements as stated under the Section VII

The Bidder shall apply a well-established component classification and identification system. The international SI system of units shall be used for design, drawings, diagrams, instruments, etc. The Plant shall be designed to achieve a high level of reliability through component redundancy, quality construction implementation, quality equipment selection, and maintainability and operability. The facility shall be designed for safe continuous operation including the capability for unforeseen shutdowns.

The Bidder shall provide first aid sets at all permanent working locations, like offices, storages and workbenches and gatehouse.

Engineering Design

The Bidder shall develop the off-grid PV-BESS-DG Power Plant’s basic and detail engineering design in compliance with this Specifications, BPDB’s review & approval and following best industry practices. The Bidder shall prepare the project’s documentation that shall include, among others, the engineering, preparation and delivery program of the engineering, guaranteed data, essential diagrams, general arrangements, design criteria and main equipment specifications.

The design of the equipment and systems of the Plant shall be based on achieving the performance guarantees as described in 2.7 Plant Performance Guarantee and its corresponding test procedures described in this tender document. The Bidder shall apply for and be responsible for successfully passing all required approvals and certifications of the authorities, the government and the related authorized institutions and organizations.

Preparatory Works

Prior to the start of construction and installation, the preparatory works shall be performed in advance so that the erection of the PV plant and can be realized as planned. At his sole responsibility the Bidder shall conduct and review, but not limited, to the following preparatory works:

- collection of general meteorological data;

- conduction of own geotechnical studies;

- conduction of drainage studies including retention basins and discharge options;

- conduction of backfill studies including compaction;

- conduction of logistics and transportation studies for time of construction;

- conduction of a cartographic surveys for the exact location of boundaries and the elevation in meters above sea level;

- conduction of own study for flooding risk and the determination of possible effects of storm water due to hundred-year floods including the determination of the respective catchment area;

- demolition of existing structures in coordination with the Employer (if required);

- the Bidder is required to prepare the Environmental Management Plan;

- the Bidder is required to prepare and follow up an Occupational Health and Safety Plan for construction and operation of the PV plant and related facilities;

- To obtain certificates and acceptances from the relevant authorities and organizations, the Contractor shall send a letter to the concerned authorities with the Project Director's involvement and The PD will assist in obtaining the necessary permissions within his jurisdiction. The contractor will bear all the expenses and fees for obtaining permission;

- BPDB will arrange/provide the necessary area for laydown, temporary storage. The contractor shall be responsible for addressing any security issues of personnel and equipment;

- data collection regarding interface points;

- due diligence of all applicable aspects;

- site preparation including compaction of soil, filling of low areas with imported fill and grading of the entire area of the site to the required levels and slopes, as required, in accordance with the building plan;

- provision of temporary laydown areas, warehouses, workshops, vehicles, equipment etc. all as necessary for the construction phase;

- disposal of demolition materials according to local environmental guidelines;

- provision of precast yard as necessary;

- provision of temporary firefighting and alarm system;

- provision of temporary site drainage, storm water and sanitary drainage all as necessary for the site;

- disposal of sewage, as necessary;

- provision of temporary water and power supply;

- provision of temporary roads, as required;

- provision of temporary site fencing including gates;

- provision of first aid, site safety and security for the construction phase as per insurance requirements;

- provision of temporary reinforced security rooms according to the authority’s requirements;

- provision of temporary spill containment pallets;

- site services as required for the construction and commissioning of the Plant such as electricity supply, potable water, instrument and service air, fuel supply, telecommunication etc.;

- provisions of at least six (6) webcam(s) for site and progress supervision from start of construction including GPRS communication system, wide angle, tilt and rotation capability, HD quality and remote-control feature at light poles, as well as appropriate record and storage capabilities.

# Specification

## Introduction

The changing climate is one of the major challenges we face today. Rise in Global average temperatures, increase in sea levels and melting of glaciers and ice sheets have underlined the immediate need to address this issue. Natural climates induced by climate change will have significant impact on economy and development of the country. Essentially, we need to tackle the problem of increasing concentration of greenhouse gas (specially carbon) emissions. To reduce carbon emission, we need to promote clean and efficient technologies and harness renewable energy sources. In order to overcome the above difficulties, Bangladesh Power Development Board has taken initiative to set up an 8 MW (AC) Off grid PV-BESS-DG Power Plant on full turnkey basis at Bhasanchar of Noakhali District in Bangladesh. BPDB will provide around 30 Acres land for this project at Bhasanchar, Noakhali.

The island's geographical location is ideally suited for an Off-grid PV-BESS-DG Power System, consisting of Solar PV, Battery Energy Storage System (BESS), and diesel generation. The high-power generation components are AC-coupled to a shared 11kV medium voltage (MV) busbar, with the mini grid-forming Battery Energy Storage System (BESS) ensuring system stability. Typically, smaller daytime loads allow excess solar energy from the Solar PV system to be stored in the BESS for use during the night. The diesel generator will provide additional support during periods of low solar output or high-power demand. The project will be executed on a turnkey basis.

Location of the Solar Power Plant

The plant will be set up on 30 acres khas land by BPDB at Bhasanchar of Noakhali District in Bangladesh located at 22.374693°N and 91.386094°E.

Proposed 8MW (AC) Off Grid Hybrid Solar Power Plant

Figure: 2.1.1 General Location

Proposed 8MW (AC) Off Grid Hybrid Solar Power Plant

Figure: 2.1.2 Specific Location

Climate Data of the proposed Site

The following climate data of the location of the SPV Plant must be considered during plant design:

| Climate Type | : | Hot, Wet and Humid Tropical Climate, Intense Sunshine, Heavy rain |
| --- | --- | --- |
| Annual Average Temperature | : | 26.270 C (Maximum) |
| Annual Average Temperature | : | 12.670 C (Minimum) |
| Average Daily Temperature | : | 25.320 C |
| Relative Humidity | : | 75% - 90% |
| Average Annual Rain fall | : | 2484 mm. |
| Maximum Wind Velocity | : | 200 km/ hour |
| Atmospheric salinity |  | Bidder will consider the salinity of the project site (Coastal region) |

## OFF GRID PV-BESS-DG POWER plant design concept

## The entire plant should be designed to function at its desired and guaranteed functional performance level with expected working/functional life considering the climatic conditions prevailing at the site. The corrosion protection level should be in consideration of the climatic condition for all the components and subsystems.

The main characteristics of the sample PV plant are defined below:

- The nominal peak power at 11kV side of the PV Plant shall be equal or higher than 8 MW (AC).

- The PV power plant will consist of fixed mounted PV modules made of Mono Crystalline cells and Bi Facial technology and string inverters.

- The PV module mounting frames and structures will be built with fixed tilt angle set in 23º and South orientation. Pre-mounted structures to ensure efficient installation can be considered.

- 16 MW Battery Energy Storage will store energy during day time when excess energy produces from the PV System and supply energy to Load.

- 3x3400 KVA LV/11 kV transformers will collect the energy produced by the solar array. These transformers will be interconnected through an 11-kV underground network. The LV side design, including voltage (which may be 400V, 800V, or other voltages), is left to the discretion of the bidder.

- 2x3400 KVA of 11/LV kV transformers connected with battery inverter will collect the energy from 11 kV bus   to charge the battery and vice versa. The transformers will be interconnected through 11 kV underground network.

- 1x1250 KVA of 0.4/11 kV transformer will collect the energy generated by the Diesel Generator to supply power to 11kV bus. The transformers will be interconnected through 11 kV underground network.

- 1x3 MVAR Static Var Generator (SVG) shall be connected at 11 kV bus to supply VAR.

- Total 4 (four) nos of 11 kV feeder and associated transformer & distribution line will deliver power to the consumer/end user.

- The water supply will comprise the construction of a pipeline network, storage and water distribution within the Plant for cleaning, cooling, cooking, and sanitary purpose.

- A fire protection system will cover the whole plant perimeter and main constructions.

- Security and surveillance system will include personnel access control, perimeter barrier protection, deterrent system, workstation and permanent alarm screening routine.

- Protection system covering: power circuits, energy storage, meteorological stations, security and surveillance and energy metering etc.

- Access road, internal and perimeter roads.

- Service building/Control Room, gatehouse.

- Drainage, Perimeter/Boundary wall.

### 2.2.1 Plant Overview

The minimum design requirements of the Plant are shown below:

| Criteria | Requirements |
| --- | --- |
| Module technology | Mono Crystalline cells and Bi Facial technology |
| Minimum PV plant output power (STC) | 8 MW AC on the MV side (11 kV) of the step-up transformer. Minimum 10MWp (STC) |
| Minimum module efficiency (STC) | Monocrystalline 22.50% |
| Module PID resistance | Mandatory, third-party tests required as per international standards |
| PV Plant output degradation | 90% of the initial yield after 10 years and 85% after 25 years |
| Grid Tied Inverter technology | String inverter Euro Efficiency > 97.5%, minimum 250kVA |
| Battery Inverter technology | String inverter Euro Efficiency > 97.5%, minimum 200 kVA |
| Minimum BESS Charging/Discharging output | The minimum configuration for the step-up transformer on the MV side (11 kV) will consist of at least two parallel units, providing a total of 5 MW AC |
| Battery Technology | LFP |
| BESS Capacity | Minimum 16 MWh on the MV side (11 kV) of the step-up transformer (Capacity of Each Unit: Maximum 2MWh) |
| Capacity Degradation | Should retain 70 % of Nominal nameplate capacity after 10 years with a yearly linear degradation |
| Depth of Discharge (%) | 85% |
| Round Trip Efficiency | Minimum 90% |
| Diesel generator | 1.256 MVA with ancillary equipment and diesel storage tank. (DG shall have diesel storage capacity for minimum 15 days of continuous operation in full Load). |
| Module Mounting structure | Ground mounted, Fixed tilt, pre-mounted structures to ensure efficient installation can be considered. |
| Connection Voltage | 11 kV |
| Cable losses | Maximum cable losses 5%. |
| Environmental Conditions | Marine environment and hot climate |
| Design Life of the Plant | Minimum 25 Years, |
| Compatibility | All selected and installed equipment shall be compatible to each other and shall not limit single items in its capability. |
| Reliability and redundancy of system configuration | The plant configuration shall be designed for reliability and redundancy. - The BESS must have a modular and redundant design so that failure of any single component shall not reduce capacity by more than 20% (or the 1/ number of indivisible components of one type, whichever is larger), and so that faulty parts can be replaced through isolation of the local modular component only. - The PV Generation pant must have at least two parallel transformers for 50% availability in case of transformer failure. |
| General Design | The facility shall be designed for safe continuous operation and easy maintenance, under harsh environmental and climate conditions. |
| Monitoring / PCMS /EMS | The monitored systems shall include monitor strings, grid tied inverters, battery inverter, BESS, diesel generator, installed weather station and shall comply with the Employer’s requirements. PCMS controls plant operation and optimization. PV plant dispatch commends, BESS dispatch, diesel dispatch, shut-down and start-up. |
| Security | The Contractor shall ensure that the Plant design includes suitable security systems such as fences and CCTV. A security Building at the entrance gate is required. |
| Quality | The materials and components used in the construction of the solar Plant shall be of superior quality from tier one manufacturers with strong track record. The Contractor shall consider all corrosion and erosion for the whole lifetime of the Plant. Materials to be used shall be corrosion protected, UV resistant and withstand high-temperature conditions over the whole lifetime of the Plant. All equipment shall be unused and newly manufactured for the project by renowned manufacturers. |
| Grid quality and support | The plant operation and control system shall maintain MV levels within BPDB mini grid limits of local distribution. Overall BESS and PV plant is required to provide autonomous and automatic local mini-grid support functionality for frequency, voltage control and fault ride-through events, as well as coordination of BESS dispatch and solar PV plant dispatch via PCMS. |

### 2.2.2 Electrical Voltage Level

The electrical voltage levels of the Plant are given below but it depends on the design proposed by the Bidder in its bid.  However, the output voltage of the inverter and MV transformer shall be 0.4-0.8 kV and 11 kV respectively.

- DC System: This shall be applicable from solar PV panel up to the inverter and Battery to the Battery Inverter. The operating voltage of inverters shall depend upon the maximum power point tracking (MPPT) range; however, the maximum system voltage will be limited to 1500V.

- LV System: AC Low Voltage System post PV inverter and/or BESS-PCS shall again be linked to inverter/PCS specifications; however, the output power should be three-phase with a nominal frequency of 50Hz.

- LV Auxiliary System: 400V AC low voltage for internal consumption shall be interpreted as per requirements of the installed equipment (AC, UPS, motors, pumps, etc.).

- MV System: AC Medium voltage shall be interpreted as 11 kV.

## CONTRACTOR’S AND EMPLOYER’S OBLIGATION

### 2.3.1 Employer’s Basic Obligations

Unless specified/described elsewhere in other sections of this document, the Employer shall be obliged to:

- Hand over required land for solar PV project development to the Contractor along with onsite marking of boundaries.

- Appoint a representative to communicate and cooperate regularly with the Contractor or its representatives in any manner upon reasonable request by the Contractor.

- Appoint quality assurance personnel to witness tests on all the necessary plant and equipment prior to the supply/procurement.

- Appoint an Employer's engineer to review project design and monitor the Contractor’s performance in the supply, construction, commissioning and operation of the plant.

- Maintain the cash flow of the project and make payments to the Contractor after satisfactory completion of its obligations as per the contractual payment milestones.

### 2.3.2 Contractor’s Basic Obligations

In this chapter and chapters to follow, the Contractor shall refer to the bidder who has been awarded the Contract.

In addition to obligations of contractors specified elsewhere in other sections, the Contractor shall be bounded by the following basic obligations:

- Adherence to all the chapters and with all the appendices of this bidding document is a key obligation of the Contractor.

- Bidders shall independently conduct resource assessment and predict energy yields detailing yearly losses and degradation over the project lifecycle.

- Wherever standards and codes are provided in this bidding document, the most stringent codes shall be followed by the Contractor; wherever codes are not mentioned, latest relevant local and international codes shall be followed and properly cited/referenced. In case of conflict between different standards, (i) standards defined as mandatory per Bangladeshi law shall be followed, and (ii) solar PV international standards such as IEC/IEEE shall prevail over, local standards.

- The project scope shall include everything required for the successful implementation, commissioning and operation of the plant for its operating lifecycle of twenty-five (25) years. This shall not be limited to the description provided in this document and no variation shall be entertained on this account by the Employer.

- The Contractor shall perform works strictly adhering to technical documents and drawings approved by the Employer as well as requirements established by the most stringent applicable technical standards.

- The Contractor shall strictly follow the start-up and functional requirements of the project as presented in this document. This shall essentially include all the material and construction equipment supply, implementation, testing and commissioning of the relevant systems as required for successful completion, commissioning, operation, and maintenance.

- The Contractor shall install, make available to the Employer and the Employer’s engineer and maintain the Employer’s local on-site office.  The office shall accommodate at least 4 (four) working stations, one meeting room, one kitchen with dining facilities.  The office will have facilities including all furniture, fixture, table, chair, almirah, file cabinet, printers and photocopiers, internet, whiteboard, etc.

- The Contractor shall comply with the environmental and social management plan implementation following World Bank Group’s General Environmental Health and Safety Guidelines (http://www.ifc.org/ehsguidelines), World Bank Operational Policy 4.01 and IFC Performance Standard 2 and the ESMP prepared for the project as published.  The Contractor shall keep high attention on labor management in and around project area based on the local culture, customs and religious sensitivity.

## GENERAL REQUIREMENTS

All the materials and works must be in accordance with the most advanced good industry practice for the design and construction of photovoltaic power plants. All the materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International good industry practice.

The Contractor shall be responsible for arrange construction power during the whole construction period. The associated costs for acquiring the electricity including the usage cost shall be borne by the Contractor.

- Exceptions to this Specification

Any deviation from minimum requirements of technical specification will result in the disqualification of the Bidder’s proposal. Any proposal for deviation by the Bidder from this Specification or any other document or drawing referenced in this Specification, shall be sent in advance, during the Question-and-Answer phase, clearly substantiated, in a complete and explicit way, for the Employer’s approval. All replies shall be public and known to the rest of the Bidders.

- Documents discrepancy

In case of discrepancy between the documents included in this Specification, the following order of priority shall prevail:

- Applicable legislation, only if more restrictive criteria are not established in the Data Sheets Requisition or Specification.

- Technical Specification.

- Other specifications and standards of the project.

- International Codes and Standards.

- Materials, design and sizing

- The Contractor must design the equipment in accordance with the operational conditions. The design shall facilitate comfortable access for maintenance works, and a high degree of reliability.

- The design shall meet all the required criteria to assure personnel security and safety during the different phases of the project (erection, start-up, operation and maintenance).

- All the supplied equipment and materials must be brand new and unused.

## FUNCTIONAL REQUIREMENTS

- The Solar PV Plant shall guarantee the delivery of Minimum 8 MW (AC) Power at the 11-kV side of step-up transformer.

- The BESS shall guarantee to Charge/Discharge of Minimum 5 MW (AC) at the 11-kV side of step-up transformer.

- The BESS shall guarantee the delivery of Minimum 16 MWh Energy from the Battery Energy Storage.  at 11kV side of Step-up Transformer from 100% SOC. With a remaining capacity of 70% of name plate capacity after 10th year with a yearly linear degradation

- The Plant design shall take into consideration that the site is seasonally flooded and high risk of extreme wind load from cyclone. It should allow for trouble-free operation and maintenance under any weather conditions.

- The start-up and functional requirements shall essentially meet all the supply, installation, testing and commissioning by the Contractor as required to complete the Plant.

- Following are the non-exhaustive requirements that shall be offered by bidders.

### 2.5.1 Site Preparation

Topographical survey and geotechnical investigations are to be implemented and completed by the Contractor including verification of the information delivered. The Contractor shall be liable for the accuracy of the topographical and geological information. Bidders are therefore advised to understand the site conditions with an obligatory visit to the project site before submitting their bids.

The site preparation shall include all the works as required for installation of a utility scale solar PV plant as per international practices. This shall essentially include but not be limited to:

- Earthwork: Following the site visit prior to bidding and based on previous experience, bidders are expected to estimate the volume of earthwork required. Site may require:

- Clearing of weeds, chopping down of small bushes and trees.

- Earth filling and leveling up to the existing nearby road of the project site of Bhasanchar.

- Levelling of land with excavation and back filling of soil.

- Movement of soil for levelling within the site or by bringing soil from outside.

- Grading the soil with the slope required by the PV modules and drainage.

- Back Fill of Land (or elevated structure) for all the plant’s facilities, such as 11kV substation, transformer, BESS, control buildings, internal road etc.

- Compaction of earth work shall be minimum 98% MDD.

- Rock blasting.

- Roads and Pathways: As a part of site preparation, all roads shall be designed and constructed to allow smooth onsite transportation and delivery of all project components to installation location and heavy equipment to their respective work locations.

- Site Office and Material storage: The Employer shall not be liable for any on site System. The Contractor shall have its own on-site project management office and site warehouse for material storage with required security. Maintaining the hygiene, the Contractor shall have adequate mobile toilets at multiple locations within the site.

### 2.5.2 Metrological Stations

The Contractor shall provide and install on site two (2) meteorological stations to provide adequate meteorological data to evaluate system performance. For the purpose of crosschecking the solar data, it is recommended to use independent and reliable data from www.SolCast.com. In case there is any dispute regarding the data or results, the information provided by SolCast will be considered the authoritative source for resolving such issues, as it offers verified and globally consistent solar data.

The stations shall essentially include sensors for the following parameters (as per section 2.11.16):

- global irradiation on tilted plane;

- global horizontal irradiation;

- direct normal irradiation

- air temperature and humidity;

- soil temperature;

- wind direction and speed;

- atmosphere pressure;

- atmospheric precipitation;

- evaporation from water surface; and

- atmospheric effects including the most hazardous (storms, whirl, thunderstorm activity, dust storms and etc.).

Dedicated pyranometers shall be used for measurement of global irradiation on tilted plain and global horizontal irradiation.

The meteorological stations, with their corresponding data loggers, shall be located at strategic point and shall be capable of collecting the data points at preset sample frequencies. The meteorological stations shall have capability of recording and storing environmental data without AC power for a minimum of ten (10) days.

Both the meteorological stations and the data loggers shall be tampering proof. The meteorological stations shall be integrated in the control system before commissioning. The Contractor shall provide a remote secure connection through the external internet line for data export to the main offices of the Employer at its HQ Office or any other entity that the Employer might designate. Format of the data transmission and interfaces shall be defined in agreement with the Employer.

### 2.5.3 Perimeter Wall

The Contractor is required to review and consider all historical rainfall and flooding data in order to define the Design Basis for its proposed water management System which includes drainage system, hydraulic works and flooding.

The Plant will be protected by a perimeter wall.

### 2.5.4 Drainage System

The Contractor is required to build a drainage system to manage water in the plot. Bidders are expected to study the site topography and plan the surface drains accordingly. Utmost care shall be taken to maintain slopes and to prevent water clogging at the site and to avoid erosion of any System foundation, road, dam or dike. Proper water drain channels shall be designed wherever necessary. The water drainage network shall have an outlet/ drainage sluice at a suitable location on the plot periphery to connect with the natural water flow.  However, the Contractor shall carry out the drainage study and identify the suitable location and size of the outlet/drainage sluice.

This system must ensure at least the several simultaneous goals as stated below:

- Insure personnel safety at all times, specially under heavy rain conditions;

- Prevent that no elements of the plant shall be damaged because of flooding;

- Ensure that water is properly drained from the plot and no stagnant water is retained;

- Guarantee that it shall stop incoming waves to the maximum historically recorded height;

- Guarantee that it shall prevent the formation of waves that could reach electronic equipment under maximum foreseeable storm conditions.

- Allow access for operation and maintenance; and

- Minimize environmental impact of the facility, respecting natural water pathways.

It shall also include:

- Channels to drain water towards the Existing Natural Canal;

- Inner stream-water dikes to allow gravity drainage and prevent flooding in case of heavy rain;

- Installation of sluice gates to control water levels, including a pumping system; and

- Preparing land and water flows to prevent erosion of roads, foundations, etc.

Prior to the installation of the electronic equipment of the plant, the drainage system shall be built and operational and equipped with emergency diesel generator.

### 2.5.5 Roads and Pathways

All roads shall be designed and constructed to allow smooth on-site transportation and delivery of all project components to installation location and heavy equipment to their respective work locations. At all cable crossings, Hume pipes of appropriate sizes shall be embedded within the road. The Contractor shall architect the internal roads and pathways in most endeavor way for easy operation and maintenance and safety measures.

Main road, perimeter road and internal roads shall be designed for a life of thirty (30) years. Roads shall be constructed with required cutting of soil, grading to the given slopes, backfilling and due compaction. The minimum width of main road, perimeter road and internal roads shall be 6, 3 and 3 meters respectively, excluding roadsides. The main approach will be on the either north side or south side (will decide later) of the project boundary and the width of the road’s foundation shall be 13m.

All main road shall be at least 0.5m high and all internal roads shall be at least 0.25m high from FGL to allow their uninterrupted use during rain or flood conditions. There will not be any dead-ends and access will always be possible through an alternative path.  All internal and main roads shall have sufficient culverts to drain out the rain water of the project area through the drains or canals to the pumping outlet of the project area. Maximum longitudinal slope of the road shall be less than 5%.

Perimeter road shall be at least 0.5m high from the FGL allow their uninterrupted use during rain or flood conditions. A sluice gate shall be installed at canal side of the perimeter road. The sluice will be provided with light weight flap gate on the canal side to open under water pressure when tide level permits. Pumps will be installed by the side of the sluice gate to pump out rain water out into the sluice outfall channel. A minimum number of 2 pumps including 1 standby pump having minimum capacity of 10 HP shall be installed in the pumping station.

All buildings and housings for inverters, transformers and electrical switchgear shall be connected by main and/or internal roads.

An appropriate drainage system shall be in place to protect the roads from erosion.

### 2.5.6 Mounting Structures

Given the seasonal flooding of the project site, it is necessary to supply a structural support system of sufficient height to ensure that it will work under dry and wet conditions. It is left to the Bidder to define the specifics of the proposed system, so long as it complies with the following minimum requirements:

- At no time, including flood and storm conditions, any electronic equipment shall be submerged under water;

- As a precautionary measure, in case the drainage system would not be able to impede flooding inside the Project’s perimeter under some extreme circumstance, the supporting structure must ensure that the PV modules stand at a minimum height of 1.5 m above the terrain; the Contractor will be fully responsible for the calculation of this height in a way that ensures compliance with requirement (a) of this list;

- At all times, it shall be possible to properly access all equipment and System for maintenance purposes;

- The guaranteed performance of the plant shall be achieved, irrespective of flooded or dry conditions;

- The materials shall be designed for marine-type environment; and

- Foundations and supporting structures shall be able to withstand submersion with a degradation rate compatible with their specified operational lifetime.

### 2.5.7 Inter-Row Spacing for PV Mounting Structures

In addition to optimizing the inter-row pitch for minimum shading, adequate inter-row spacing shall be maintained for cleaning of modules.  Bidders must mention the inter-row spacing and the number of PV module rows in their bids.

### 2.5.8 Lightning Protection System

The entire PV plant area including all buildings shall be protected from lightning. The protection system shall be based on early streamer emission lightning conductor air terminals. The air terminals shall provide an umbrella protection against direct lightning strike the radial distance shall be defined in the detail design and justified. The air terminal shall be capable of handling multiple strikes of lightning current and should be maintenance free after installation.

The earthing stations for the lightning discharges shall be provided with test links of phosphorus bronze and located at 150 mm above ground level in an easily accessible position for testing.

### 2.5.9 External Lighting System

All the main, perimeter and internal roads shall be lit with external lighting system strategizing site security and maintenance requirements; utmost care should be taken for avoiding any shading effect due to the poles. The light fittings shall be highly efficient having longer life. LED-based system shall be used.

Bollards of height up to 1 meter shall be installed along the main approach road towards modular plot. Additionally, flood lights may be mounted at strategic locations along the boundary of the PV plant.

Minimum of 10 lux shall be maintained around the periphery of modular unit control rooms and 4-6 lux at the main roads approaching modular unit control rooms. All the light shall be fed from power supply system available at the plant.

### 2.5.10 Earthing System

The entire PV plant area including all modular plot control rooms and MV substation shall be appropriately earthed with adequate number of earth stations. Earthing system shall comply with the latest edition of IEEE80.

The earthing system shall have complete earthing network comprising of wires, copper tapes, electrodes and earth bonding of all relevant necessary non-current carrying metal parts of equipment/ apparatus shall be connected as required.

- Specific Design Requirements

The specific design requirements for earthing shall follow:

- Earthing network within the PV plant array yard may be of GI.

- Each MV transformer shall comply with requirements in Bangladesh for earthing.

- Each MV transformer shall have a minimum of four dedicated earthing stations. Transformer body earthing can be with GI material. However, wherever star point is required to be earthed, strictly copper should be used.

- All the earth pits shall be appropriately connected.

- Dedicated earthing stations shall be provided for lightning protection system.

- All the earthing stations shall be provided with test links of phosphorus bronze and located at 150 mm above ground level in an easily accessible position for testing.

- Specific Construction Requirements

The specific construction requirements for earthing shall follow:

Plate Type Earthing Stations:

- Earthing Plate electrodes will comply with IEC 60364 and shall be made of tinned copper plate of not less than 600 x 600 x 3 mm size for copper and 600 x 600 x 6 mm for GI. The plate shall be buried vertically in ground below permanent moisture level at a depth of not less than 3 meters to the top of the plate, the plate being encased in charcoal to a thickness of 300mm all round.

- The tinned copper plate should be brazed with the bottom of the GI pipe using silver alloy.

- The joints and the interconnection of the copper strip & earth electrode are to be properly brazed & tightened/welded as applicable and covered with non-corrosive material.

- Earth leads to the electrode shall be laid in a heavy-duty GI pipe and connected to the plate electrode with brass bolts, nuts and washers. A GI pipe of not less than 50 mm in diameter shall be clamped with bolts vertically to the plate and terminated in a wire meshed funnel.

- The funnel shall be enclosed in a masonry chamber of 450mm x 450mm dimensions. The chamber shall be provided with GI frame and CI inspection cover. The earth station shall also be provided with a suitable permanent identifications label tag.

Pipe Type Earthing Stations:

- Electrodes will comply with IEC 60364 and shall be made of class C G.I. Pipe of 100 mm internal diameter. The pipe electrode shall be as far as practicable embedded below permanent moisture level. The length of the pipe electrode shall not be less than 3m.

- The earth pit will be 1 meter in diameter.

- The GI pipe is to be provided with continuous holes of 12mm dia.  In zig-zag fashion, spacing 15cm apart, starting from the bottom up to height of 2 meters.  A single run of the earth conductor of 25x3mm copper strip with high insulation PVC sleeve, should be provided along with the GI pipe, interconnecting the GI strip at the top of the GI pipe and earth electrode at the both of the GI pipe and strip. The above conductor and GI pipe are to be suitably brazed at the bottom side with the earth electrode mentioned below. The earth conductor and the GI pipe are to be clamped with each other with 16SWG GI wire at regular intervals of 600mm. A GI funnel of suitable size to pour water into the earth pit is to be welded at the top of the GI pipe.

- The pipe electrode shall be made of one piece. Earth leads to the electrode shall be laid in a heavy-duty GI pipe and connected to the pipe electrode with brass bolts, nuts and washers. GI pipe shall be terminated in a wire meshed funnel.

- After positioning the entire assembly as above, the earth pit will be filled with charcoal, salt & Bentonite homogeneously/alternatively.

- The pit shall be enclosed in a masonry chamber of 450mm x 450mm dimensions. The chamber shall be provided with GI frame and CI inspection cover. The earth station shall also be provided with a suitable permanent identifications label tag.

- The earth conductor will be 25x3mm tinned copper strip with high insulation PVC sleeve and shall be routed through underground pit (2ft below ground level) and laid up to the main earth bus.

- Testing

The earthing stations and the earthing network shall be tested for following on completion of the installation:

- Earth resistance of electrodes

- Continuity of conductors, joints etc.

- Drawing Submission and Identification

Each pit is to be identified by a suitable display board with details like Pit No. Power Earth, Earth resistance value etc.  The Contractor shall submit the following in the design stage to the Employer for approval.

- Site plan indicating earth pits, earthing strip routing, road cross overs etc.

- Earthing calculations along with schematic drawing for the entire network

- Drawing showing the dimensions, materials and position of all components, earth electrodes, earth conductors etc.

### 2.5.11 Water Supply and Septic System

Water Supply and storage tanks are under the responsibility of the Contractor. Water must be sourced and treated to allow human consumption and other uses in the Facility. The Contractor will furnish a water treatment plant with capacity to produce enough water to cover all the Facility’s consumption.

Water waste from the Facility shall be conducted to septic tanks.

### 2.5.12 Fire Fighting and Detection System

The solar PV plant shall be equipped with suitable fire protection and fighting systems as per the Bangladesh National Building Codes (BNBC) standard, the National Fire Protection Association (NFPA) fire safety standard and local fire authority requirements.

Fire-fighting for transformers and other electrical equipment shall be in accordance to NFPA 70 and NFPA 15.

Transformers extinguishing systems and other electrical equipment shall be designed considering industry guidelines acting in Bangladesh.

Manual call points, detectors and outdoor hooters shall be provided for all the prefabricated buildings housing the inverters. These shall be integrated with the PCMS system.

### 2.5.13 Plant Layout

The Contractor shall submit drawing showing the proposed Project Plant Layout for Employer’s approval.  The Project Plant Layout shall also be submitted with the Bid identifying all major components of the Plant.

The Plant layout shall be a comprehensive drawing showing various requirements of the project like, Reference coordinate grid, Geographical and Plant North, Boundary fence including coordinates of all corner points, Main Entrance Gate and any other access gates as per project needs, Block wise finished ground level (FGL), Internal and peripheral roads, Security Room/ cabin(s), all buildings with coordinates, temporary storage yard/ facility to be used by the Contractor during construction, proposed Array layout, Lightening Arrester etc.

The drawing shall also include the Plant Substation and cable routings from the plant transformers to the inverter. The Plant Layout drawing shall be in suitable scale to have proper representation of the information.

### 2.5.14 Electrical Lines

The Contractor shall submit a drawing showing the proposed line plan and profile drawings for the distribution line from the Plant’s substation to the end mile consumer.

Distribution line from the Plant’s Substation to the consumer shall be through 4 Nos of 11 kV Feeder of single circuit line.

The pole of the distribution line (11 kV) will be designed and equipped to hold 0.4 kV circuit.

The Contractor will supply and construct of 11, kV, 11/0.4kV and 0.4 kV Distribution Line and install distribution transformer of different capacity.

The obtention of permits for the construction of the distribution line and the corresponding works shall be the responsibility of the Contractor.

## RESOURCE ASSESSMENT

The latest Typical Meteorological Year (TMY) data from Metronome shall be used to conduct the resource assessment.

## PLANT PERFORMANCE ASSESSMENT

2.7.1 PV Plant Performance Assessment

See Appendix 9 of Bid Volume 1

### 2.7.2 BESS Guarantee Performance Test

See Appendix 10 Bid Volume 1

### 2.7.3 Start-Up of The Plant

The Contractor and the Employer (or the Employer’s Engineer on their behalf) will jointly carry out commissioning inspections and testing prior to initial operation.

The Contractor shall provide test procedures to the Employer/ Employer’s Engineer with the anticipation required in the Contract.

The commissioning inspections will verify that:

- All equipment shall be properly listed, identified and labeled, suitable for the conditions of use, and be installed according to the listed product instructions;

- All equipment shall be installed in a neat and workmanlike manner, consistent with quality craftsmanship standards in the electrical construction industry;

- All equipment shall be mechanically secured and provided with adequate ventilation or cooling as required;

- All electrical terminations and connections shall be made using approved products and installation methods. This includes consideration of conductor and terminal materials, temperature ratings, and use of specially approved terminal for use with fine stranded conductors or more than a single conductor. Pressure connectors using a setscrew have required tightening torques, and these values should be recorded and verified at commissioning;

- All electrical equipment shall be marked with the manufacturer’s identification and applicable specifications and ratings;

- Sufficient working spaces shall be provided about any electrical equipment that is likely to be serviced or maintained while energized. Clear spaces and dedicated spaces are also required about certain electrical equipment, such as panel boards or switchgear; and

- Any other inspection required by the applicable regulations, codes and good engineering practice.

Upon completing the inspections, installed equipment will be tested prior to initial operation. The tests will include:

- Continuity and resistance testing to verify the integrity of grounding and bonding systems, conductors, connections and other terminations.

- Polarity testing to verify the correct polarity for PV dc circuits, and proper terminations for dc utilization equipment;

- Voltage and current testing to verify that PV array and system operating parameters are within specifications;

- Polarity testing to verify the correct polarity for BESS circuits and proper terminations for BESS equipment;

- Voltage and current testing to verify that BESS system operating parameters are within specifications;

- Insulation resistance testing to verify the integrity of wiring and equipment, and to detect degradation and faults due to wiring insulation; and

- Any other measurement required by the applicable regulations, codes and good engineering practice.

Once the Contractor obtains the permit to connect the plant to the mini grid, the start-up testing can commence, beginning with switchyard, inverter / transformer stations and panel arrays, packet plants, pumping stations, etc.

It shall be the Contractor's responsibility to arrange all the consumables, instrumentation, material and human resources as required for completing the commissioning, start-up tests and performance ratio comparisons. The Contractor shall provide to the Employer the calibration certificates for all measuring instruments at least 21 days prior to the start of commissioning phase.  Such calibration certificates shall not be older than 90 days prior to submission to the Employer.

### 2.7.4 Performance Test

The Contractor shall, in consultation with the Employer and Owner’s Engineer carry out performance tests.

The performance test shall verify whether the solar PV-BESS-DG plant and associated equipment's are performing at or above the agreed value and is suitable for Operational Acceptance. The Contractor will provide the test procedures to the Employer/Engineer at least 21 days prior to start.

It will be conducted as specified below.

- Measured meteorological data shall be used on the PV Syst model in order to obtain a theoretical production value. This value shall be compared versus the actual production value during the test.

- On-site measuring instrumentation shall include a secondary class pyranometer, temperature sensor, data logging systems and energy tariff meter.

- The Contractor may only start the performance test only after achieving physical completion and synchronizing the Plant with the 11-kV mini grid by complying with all relevant requirements from employer.

- The Performance test of the Solar PV System shall be conducted for a minimum of ten (10) consecutive days of operation during daylight hours (Irradiance levels greater than 200W/m2). The operation data shall be recorded at 15-minute intervals for validating the production values. In the event of load insufficiency, a modular performance evaluation aggregating 8 MWac of the Solar PV System shall be conducted.

- The Performance test of the Solar PV/BESS shall be conducted for a minimum of ten (10) consecutive days of operation during day/night until a maximum power supply reached at 8 MW for solar and 5 MW for BESS. In the event of load insufficiency, modular performance evaluation aggregating 16 MWhr of the BESS System will be carried out.

- The required diesel shall be provided/supplied by the contractor during the performance testing of the diesel generator set.

The Performance tests will consist of:

            - Solar Photovoltaic System

- AC power output

This test will record the applicable derating factors, such as:

  - Nameplate Ratings;

  - Inverter and Transformer;

  - Module Mismatch;

  - Wiring;

  - Soiling;

  - Etc.

The Estimated System AC Power Output at STC - 1000 W/m2, 25°C (kW) will be adjusted for temperature and measured radiation and the final result will be compared with the actual recorded readings.

- AC Energy Production

This test will use the same derating factors. The resulting estimated daily output with the measured radiation and temperature will be compared to the actual readings.

- Array I-V Measurements

The intensity vs. voltage curves will be used to analyze:

  - True array maximum power point;

  - Identify array wiring problems or module failures;

  - Evaluate losses due to module mismatch and array wiring methods;

  - Locate open bypass diodes;

- Thermal Imaging

Thermal imaging will be used to identify hot spots or overheating equipment and thermal gradients within PV arrays, to locate defective PV modules.

- Inverter Efficiency Tests

Efficiency measurement will be made in the field by simultaneously measuring the dc power input and ac power output at the inverter terminals.

- Any other test required by the employer, applicable regulations, codes and good engineering practice.

Solar data shall be input in the PV Syst model supplied by the Contractor, and theoretical production values from the model shall be compared with measured production values.

            - Battery Energy Storage System (BESS)

- AC power output

This test will record the applicable derating factors, such as:

  - Nameplate Ratings;

  - Inverter and Transformer;

  - Wiring;

  - BESS consumption;

  - Etc.

- Storage Capacity Test (SCT)

Each Storage Capacity Test shall be conducted in accordance with Prudent Utility Practices.

- The measurement of charging energy required to charge the BESS up to the Maximum Stored Energy Level

- The measurement of discharging energy from the BESS to the Point of Delivery (11kV) until the Stored Energy Level reaches zero MWh as indicated by the battery management system.

- Electrical output at Maximum Discharging Capacity at the high-tension side of 11 kV step-up transformer;

- Electrical input at Maximum Charging Capacity at the on high tension side of 11 kV step-up transformer;

- Amount of time between the BESS’s electrical output going from 0 to Maximum Discharging Capacity;

- Amount of time between the BESS’s electrical input going from 0 to Maximum Charging Capacity;

- Amount of energy required to go from 0% Stored Energy Level to 100% Stored Energy Level charging at a rate equal to the Maximum Charging Capacity.

- Round Trip Efficiency:

The total amount of Energy Out divided by the total amount of Energy measured at the high-tension side of 11 kV step-up transformer pursuant to a Storage Capacity Test. The minimum round-trip efficiency shall be 90%.  Round Trip Efficiency shall be calculated during commissioning and FAC in accordance with the ANNEX V;

In case of disruption due to any component failure, the test shall be repeated.

- The production values shall be computed based on actual energy exported to the 11kV Local grid at the metering point.

- Subsequent to operational approval, regular production monitoring shall be performed and reported to the Employer, according to schedule presented in and the reports on daily, weekly, monthly, quarterly and annual basis.

- If the Contractor fails to achieve the guaranteed performance levels, the Contractor shall at its own cost rectify all the defects identified during the test and take necessary steps/efforts to pass the test within the stipulated time span. Subsequent to rectification the production shall be re-tested, if the values are again below the guaranteed performance levels, the Contractor shall be liable to pay liquidated damages the Employer as agreed within per the Contract.

## FUNCTIONAL WARRANTIES

As per Technical Guarantee Parameters of the PV system of Bid Volume III

(Technical forms to be filled attached in the appendix)

The solar PV-BESS-DG Power Plant project shall be implemented through a contract and comprehensive warranties of two (2) years from the date of commissioning and commercial operations (i.e. Operational Acceptance). The project warranties shall essentially include but shall not be limited to:

## 2.8.1 Defects Warranty

The contract shall provide a two-year comprehensive warranty for the entire solar PV-BESS-DG plant. The Contractor shall warrant the project free from any and all defects including unseen and latent in all project components and workmanship.

In case of any manufacturing defect or underperformance of any project component, the Contractor shall guarantee supply, installation, testing and commissioning of replacement project component/s replacing the corresponding defective project component/s at no cost to the Employer as per Contract conditions.

In case of defects due to improper handling of project components by Contractor’s team during warranty period, the Contractor shall be responsible for repairing any/all defects. The Employer has the right to get monetary compensation for loss of energy generation caused due to plant unavailability as per Contract conditions.

Any replacement made, or component repaired by the Contractor shall continue to be in warranty for the balance warranty period along with an additional extended warranty for twelve (12) months with no charge to the Employer. The extended warranty shall come in effect upon expiry of original warranty period. The PV panels shall have an extended warranty of 25 years as per Contract conditions.

## 2.8.2 Project Components Warranty

Project components warranty can essentially be construed as guarantees / warranties provided by the project component manufacturers beyond the defect liability period, performance warranty period and extended warranties.

Key components shall be factory tested according to the approved Quality Assurance Plan before shipping to ensure their compliance with the technical specifications.

Warranties and conditions thereof for key project components are separately specified in the general technical specification of key project components.

Any and all such warranty for any of the project components shall be transferred to the Employer after completion of the warranty period.

The Employer shall reserve the right to call for extended warranties from the manufactures and the same shall be agreed by the Contractor and product manufacturer.

## 2.8.3 Production Warranty

- Production from Solar PV System

The bidder is required to propose a PV Plant with a capacity ≥ 10 MWp and performance ratio (PR) ≥ 80% at the time of commissioning regardless the month the Plant is commissioned. This is a Technical Mandatory Requirement subject of rejection if not compliant.

See Appendix-9 for PR calculation of PV plant

- Energy Stored in and supplied from BESS

Guaranteed Dischargeable Energy” and “Minimum Round-Trip Efficiency Performance Guarantee” shall be measured at 11 kV side of step-up transformer as per ANNEX IV for the applicable Contract Year. Minimum Round-trip Efficiency shall be calculated during commissioning and FAC.

## OPERATION AND MAINTENANCE

Bidders shall submit the operations and maintenance schedule for the overall project detailing that of all project components. This planning will detail the expected maintenance works, such as cleaning, inspections, yearly repairs, etc. Bidders shall also submit the cost estimates for operations and maintenance during the 25-year operational lifetime of the plant.

### 2.9.1 PV Module Cleaning

Employers shall follow the PV Module manufacturer’s instructions and recommendations for routine cleaning.

The cleaning method and process shall be detailed in the O&M manual.

### 2.9.2 Training

During the first two (2) years of defect warranty period, the Employer shall appoint personnel to be trained in the operation and maintenance of the plant.

    - Overseas Training

Foreign or overseas Training Venue will be at Manufacturer's Factory Premises. All living, accommodation, food, transport expenses of the trainees/officers during the period of training/study tour including airfares, incidental expenses, medical expenses, medical insurance etc. will be covered by the Contractor including pocket allowance of @ USD 100.00 day/person. The total person-months for training will be limited to 12 (twelve) Person-Months for 14 persons on PV Module, Inverter, BESS, Switchgear, Distribution System and Operation & Maintenance of power plant equipment, orientation & technology transfer at manufacturer's factory

    - Training at the Site for O & M

Note. Detailed Training Program (including subject, duration, place of training, training methodology, Trainers’ qualification/ experience) shall have to be mentioned by the Tenderer.

## WATER SUPPLY, WATER DRAINAGE AND WATER TREATMENT SYSTEMS

### 2.10.1 Water quality requirements and water flow

The following systems of water supply shall be provided in the Plant:

- Drinking water supply providing water to meet the needs of the buildings and facilities on the site;

- Firefighting water supply.

### 2.10.2 Drinking water supply

Drinking water shall comply with Bangladeshi standard requirements.

The Plant preliminary design demand in domestic water shall be calculated in accordance with local requirements. Supplied drinking water to the site shall also be used for sanitary purposes, i.e. showers, sinks, toilets.

### 2.10.3 Firefighting water supply

The source of firefighting water supply system for the site shall be firefighting water tanks with the needed capacity which shall contain adequate water supply for firefighting.

Calculations for Firefighting water reserve and pumps (with electrical motor and engine driven) shall be carried out by the Contractor and justify the fulfillment of these requirements to local standards as well as international standards.

### 2.10.4 Water drainage system

The following facilities shall be designed on the Project site:

- Administrative Office sewage system for waste diversion;

- Rainwater drainage;

- Oil emergency drains;

- Septic tanks.

The Contractor shall design and construct rainwater drainage network for smooth disposal of rainwater from the Plant to the nearest available drainage outlet. The rainwater drainage system shall be designed and planned to ensure no water stagnation in the Plant. Necessary input data for maximum hourly rainfall intensity to be taken for drainage design shall be obtained by the Contractor from Bangladesh Metrological department.

The drainage system shall be designed as per the provisions of relevant Bangladesh standard and best Industry practices.

The drainage scheme shall be designed considering the Plant plot area and the catchment area contributing to the Plant area drainage. The rain water drainage system shall be a network of open surface drains (with rectangular or trapezoidal cross section) and shall generally be designed to follow the natural flow of water and ground contours.

The proposed drainage scheme along with design calculations shall be submitted to the Employer for review/ approval before start of construction.

### 2.10.5 Office/Administrative Building sewage system

Office/Administrative Building wastewater from buildings and structures shall be sent to the septic tanks.

### 2.10.6 Rainwater drainage

Rainfall run-off from roads, roofs of buildings and structures will be collected in trough gutters and discharged as per the drainage design to be reviewed and approved by the Employer’s Engineer.

To dispose of accumulated internal rainwater and an outside inflow of about half square kilometers, a single Vent of minimum 2.44-meter-wide x 1.60-meter-high conduit type drainage sluice may be provided at the end of the drain outlet. The sluice will be provided with light weight flap gate on the sea side to open under water pressure when tide level permits. The size needs to be checked and verified during detail design. When the level does not permit drainage, pumps will be installed by the side of the sluice gate to pump out rain water out into the sluice outfall channel. A minimum number of 2 pumps including 1 standby pump having minimum capacity of 10 HP shall be installed in the pumping station.  The number of pumps is considered of 300mm rainfall by day.  The sluice outfall channel may need to be re-excavated up to the estuary to have efficient drainage.  The Contractor will carry out sluice site survey work (grid survey) for an area 100-meter x 100 meter from the center line at the plant section. It may be a plane table survey with spot level taken at every 5-meter interval. The Contractor will also conduct geotechnical investigation at the sluice site (three bore holes to be done with Standard Penetration Test (SPTs) extending to 20 meters with samples taken at every 5 meters for testing) to design the foundation of the Sluice.

## Technical Specification

The Grid Tied Solar Photovoltaic power plant consists of the following’s equipment and accessories but not necessarily be limited to:

- Solar Photovoltaic (PV) Module

- Module Mounting Structure

- Grid Tied Inverter

- Battery Inverter

- Battery Energy Storage System (BESS)

- Diesel generator

- EMS

- Transformer

- LV/MV Switchgear

- LV/MV Cable and Accessories

- Plant Control and Monitoring System

- DC, UPS, & Auxiliary Power Supply

- Protection and Control System

- Static Var Generator (SVG)

- Fire Fighting System

- Security and Surveillance

- Emergency Diesel Generator

- Weather Station

- Distribution System

- Lighting and Illumination System

- Metering System

- Civil Works

### 2.11.1 Solar Photovoltaic (PV) Module

Monocrystalline solar PV technologies can be used which fulfill the performance parameters presented in below chapters.

#### Quality Certification

PV modules shall typically be tested for durability and reliability according to standards developed by the International Electro-technical Commission. Standards IEC 61215 (for crystalline silicon modules) and the appropriate IEC for the other technologies include, amongst others, tests for thermal cycling, humidity and freezing, mechanical stress and twist, hail resistance and performance under fixed test conditions.

The list below summarizes major PV codes and quality standards that all the modules shall comply. These tests are an accepted quality mark and indicate that the modules can safely withstand extended use.

- EN 50262 Cable glands for electrical installations

- EN 50380 Datasheet and nameplate information for photovoltaic modules

- IEC 60068 -2-68 Environmental testing - Part 2-68: Tests -Test L: Dust and sand

- IEC 60216-1 Electrical insulating materials - Properties of thermal endurance - Part 1: Ageing procedures and evaluating of test results IEC 60364-4-41 Protection against electric shock

- EN 60695-1-1 Fire hazard testing

- IEC 60529 Degrees of protection provided by enclosures (IP code)

- IEC 60891 Procedures for temperature and irradiance corrections to measured I-V characteristics of Photovoltaic (PV) devices

- IEC 60904-1 Part 1: Measurement of Photovoltaic Current-Voltage Characteristics

- IEC 60904-2 Part 2: Requirements for reference solar devices

- IEC 60904-3 Part 3: Measurement principles for terrestrial Photovoltaic (PV) solar devices with reference spectrum irradiance data

- IEC 60904-4 Part 4: Reference solar devices – procedures for establishing calibration traceability

- IEC 60904-5 Part 5: Determination of the equivalent cell temperature (ECT) of photovoltaic (PV) devices by the open-circuit

- IEC 60904-7 Part 7: Computation of the spectral mismatch correction for measurements of photovoltaic devices

- IEC 60904-8 Part 8: Measurement of spectral response of a photovoltaic (PV) device

- IEC 60904-9 Part 9: Solar simulator performance requirements

- IEC 60904-10 Part 10: Methods of linearity measurement

- IEC 60943 Guidance concerning the permissible temperature rise for arts of electrical equipment, in particular for terminals

- IEC 60990 Methods of measurement of touch current and protective conductor current

- IEC 61140 Protection against electric shock - Common aspects for installation and equipment

- IEC 61215 Crystalline silicon terrestrial photovoltaic (PV) modules – Design qualification and type approval

- IEC 61345 UV test for Photovoltaic (PV) modules

- IEC 61646 Thin film terrestrial photovoltaic (PV) modules - Design qualification and type approval

- IEC 61701 Salt mist corrosion testing of photovoltaic (PV) modules

- IEC 61730-1 Photovoltaic (PV) module safety qualification - Part 1: Requirements for construction

- IEC 61730-2 Photovoltaic (PV) module safety qualification - Part 2: Requirements for testing

- IEC 61853-1 Photovoltaic (PV) module performance testing and energy rating - Part 1: Irradiance and temperature performance measurements and power rating

- IEC 62109-3 Safety of power converters for use in PV power systems – Part 3: Particular requirements for PV modules with integrated electronics

- IEC 62716 Ammonia corrosion testing of PV modules

- IEC 62759 Transportation Testing of PV Modules

- IEC 62775 Measurement of EVA crosslink density

- IEC 62782 Dynamic Mechanical Load Testing of PV Modules

- IEC 62788-1-2 Measurement of encapsulant and back sheet resistivity

- IEC 62788-1-4 Measurement of encapsulant optical transmission

- IEC 62788-1-5 Measurement of encapsulant shrinkage during processing

- IEC 62790 Junction Boxes for PV modules – safety requirement and tests

- IEC 62804 System Voltage durability test for crystalline silicon modules

- IEC 62805-1 Measurement of haze of TCO glass

- IEC 62805-2 Measurement of transmittance and reflectance of TCO glass

- Any standard and code adopted by Bangladesh Sustainable and Renewable Energy Development Authority (SREDA).

Solar PV modules are required to be listed by Underwriters Laboratories (UL), or another equivalent recognized Laboratory.

IEC 61853 standards for PV module performance testing and energy rating are under development with Part 1: Irradiance and temperature performance measurements and power rating is set to release soon. Delivery of modules subsequent to release should comply with this standard.

In case international standards do not exist or inapplicable, recognized national standards shall be proposed by the Contractor and approval shall be provided by the Employer/Employer’s Engineer.

#### Guarantee Benchmarks

- Product guarantee

The Contractor shall be legally bound to provide a linear performance guarantee ensuring that entire plant shall be fully functional with desired output for 25 years from the date of commissioning (i.e. Operational Acceptance). Consequently, irrespective of manufacturer’s guarantee to the Contractor the PV modules shall be guaranteed against any manufacturing defect for at least 12 years. Defects liability shall include but not limited to glass, frame bowing, de-lamination, water ingress, junction box arching, hot spots, etc.

The product guarantee shall not be limited for modules but shall also include termination connectors, cables and all associated accessories. In the event of failure during the guarantee period, manufacturer shall replace module free of cost or refund the then current market price of modules.

- Nominal power guarantee

In addition to the product guarantee, manufacturers shall grant linear nominal power guarantees for a minimum period of two (2) years. Under these guarantees manufacturer shall ensure that module shall deliver nominal power output based on manufacturer’s provided annual degradation rate. The output shall be measured at string level. The nominal power guarantees shall be in lieu of manufacturing defects and workmanship; the minimum set terms shall be as below:

- At the end of one year from the date of commissioning, if any module produces a nominal power output below 98% as set out in manufacturer's data sheet, the Contractor / manufacturer shall replace module free of cost with a new guarantee for balance period.

- 1 to 25 years - for a period of twenty-five years from the date of commissioning the maximum allowed annual degradation for the 1st year is 2% and thereafter maximum .5% annually. If any module production falls below, Contractor / manufacturer shall replace module free of cost with a new guarantee for balance period.

PV modules must be eligible to be insured for above warranty terms by a registered insurance company having a minimum rating of ‘A’ by Standard and Poor’s, Moody’s or Fitch.

- Product life

Although, the plant shall be guaranteed for two (2) years and power performance shall be guaranteed for 25 years, upon being awarded, and prior to contract negotiation, the Contractor shall submit the manufacturers’ accelerated lifetime laboratory test reports.

#### Technical benchmarks

- Nominal Power Tolerance

The nominal power tolerance of modules shall not be beyond +3%, however preference may be given to manufacturers giving the least tolerance and tolerance at higher side.

- Efficiency

Minimum acceptable efficiency of all the modules under standard test conditions is 22.5% for Monocrystalline.

- Temperature Coefficients

Variation in temperature has a significant effect on electrical parameters of PV modules; following are the expected temperature coefficients for all the proposed modules by manufacturers:

- Temperature Coefficient of Pmax - 0.29%/°C or better

- Temperature Coefficient of Voc - 0.25%/°C or better

- Potential Induced Degradation (PID)

Panels shall be resistant to PID.

#### Specific Construction Requirements

In addition to the best construction requirements of respective manufacturers, following are the specific requirements for all the crystalline modules:

- All the modules shall be equipped with IP68 or higher protection level junction box and appropriately sized output power cable of symmetric length with twist locking connectors of a well-known manufacturer like Multi contact; Bizlink, Leoni etc.

- Fill factor for proposed PV modules shall not be less than 0.7.

- In order to minimize power loss due to partial shading on modules, all modules shall be equipped with bypass diodes.

- Modules shall be capable of withstanding a wind pressure of 2400Pa or the maximum recorded local wind loading, whichever is greater.

- Modules may be subject to high intensity hail storms or cyclones; thus, appropriate measures should be taken for selecting glass.

- Module frames shall be resistant with corrosion and salinity. Those shall have adequate holes for mounting, water drain and connecting ground conductor. All modules shall be appropriately grounded.

#### General Instructions

#### Submission

In addition to the techno commercial offer all the manufacturers shall submit following valid up to date documents:

- IEC Certificates

- Technical literature giving complete specifications and information of modules

- Handling plan of modules right through from loading at manufacturer's factory to the point of installation.

- General Arrangement drawing of module, showing front and rear view, overall dimensions, installation plans, termination arrangements, packing dimensions and weights.

- Independent test characteristics:

- Current verses voltage at various irradiance levels.

- Power verses voltage at various irradiance levels.

- Open circuit voltage verses irradiance under standard test conditions.

- Short circuit current verses irradiance under standard test conditions.

- Power verses temperature variation.

- Open circuit voltage verses temperature variation.

- Short circuit current verses temperature variation.

- Upon securing the contract, the Contractor shall also submit installation manual and flash lists of the modules.

Identification and Traceability

Each PV module must use a RF identification tag (RFID), which must contain the following information:

- Name of the manufacturer of PV Module

- Name of the Manufacturer of Solar cells

- Month and year of the manufacture (separately for solar cells and module)

- Country of origin (separately for solar cells and module)

- I-V curve for the module

- Peak Wattage, Im, Vm and FF for the module

- Unique Serial No and Model No of the module

- Date and year of obtaining IEC PV module qualification certificate

- Name of the test lab issuing IEC certificate

- Other relevant information on traceability of solar cells and module as per ISO 9000 series.

Testing

Tests shall be performed to guarantee high quality of PV modules. The number of photovoltaic modules for non-destructive tests shall be at least twenty (20) modules per batch. The modules shall be selected according to the instructions of the Employer/Employer’s Engineer from different delivery lots. The independent tests shall include as a minimum the following measurements and shall be performed in an accredited independent laboratory.

- Electroluminescence and PID Testing

- Power at STC (Flash Test)

- Irradiation performance (I-V Curve)

- Temperature coefficient

- Bypass Diode Test

- Insulation Test, Low Irradiance Test, Wet Leakage

Details of each test:

Electroluminescence Testing:

The modules shall undergo EL-inspection. A major defect shall be defined as:

- a crack, causing an inactive area of any cell (as seen in black color of the cell in the EL picture); or

- interruption 5 or more cell fingers in any areas of the cell; or

- interruption 3 or more cell fingers in the outer areas of the cell (between busbar and edge cell).

In case one or more major defects in one of the modules is reported, the Contractor may inspect all modules of the shipment within three (3) days and remove the modules with defects and replace with new modules prior to installation.

PID Testing:

PID test according to IEC 62804: The maximum accepted power loss is 5%; the test shall comply with the applicable version of tests offered by IEC 62804. Average measured PID will not exceed 1.5%.

Bypass Diode Test:

The temperature of the bypass diodes under hot-spot conditions shall be tested and evaluated according to IEC 61215. Therefore, the module shall be heated up to 75°C and a current equal to the short circuit current measured at STC shall be applied for 1 hour. Thereafter, the current shall be increased to 1.25 times the short-circuit current of the module for another hour, maintaining the module temperature at the said temperature level. The diode shall be still operational.

Flash Test:

Actual power: The MWp-DC-STC is the flash-tested DC power capacity of the installed modules at Standard Testing Conditions. The Crystalline Module shall be flash tested for STC-power after arrival on site. The STC-power shall be measured on a class AAA simulator (IEC 60904) which is calibrated with a primary calibrated reference cell (reference cell for example calibrated by NREL/USA or AIST/Japan or comparable institution providing first level calibration, uncertainty of Isc max. 1%) by an independent laboratory.

Low Irradiance Testing:

Power at 200 W/m²: For the 2nd real power sample the efficiency at 200 W/m² shall be measured with the test procedure similar to Flash Test and must be equal or more than 95% of the efficiency at STC for more than 90% of the samples.

Insulation Test:

According to IEC61215: Minimum insulation shall not be less than 40 MOhm for every square meter.

Wet Leakage Test:

According to IEC 61215: In wet condition, minimum insulation shall not be less than 40 MOhm for every square meter.

At least 10 modules out of the non-destructive tested modules shall undergo a destructive test. The modules shall be selected by the Employer’s Engineer. Following tests shall be carried out:

- Back sheet test

- Gel content of EVA layer (≥70% after polymerization)

For the destructive tests according to the list above, such necessary modules shall be supplied by the Contractor. All Costs of the Quality assurance for PV modules on-site and in laboratory shall be borne by the Contractor.

The Off-Site Testing:

The PV module testing shall be performed by the accredited independent third party. All costs associated with the independent tests shall be borne by the Contractor. The test report shall be submitted to the Employer/Employer’s Engineer for approval. The Contractor shall organize and facilitate the Employer/Employer’s Engineer visit and/or testing at the factory, if required by the Employer.

However, it shall be noted that a standard UV pre-conditioning according to IEC standards is not reflecting the conditions of PV module installation under desert conditions. Therefore, the Employer’s Engineer recommends to carry out extended test procedures at least for UV light exposure and temperature testing, which the conditions of all tests shall be close as much as possible to the site conditions in order to ensure PV modules to withstand the site environment.

The following tests shall be carried out, but not limit to, as listed below:

- UV light exposure from module front and back (IEC standard is 1,500 W/m² for de-sert conditions > 1,000 W/m² would be recommended)

- Module behavior test (irradiation and temperature)

- Module performance tests (I-V curve)

- Module electroluminescence tests

- Module thermography tests

- Temperature coefficient

- Power at STC

- Back sheet test (according to type of module)

- Gel content of EVA layer (≥70% after polymerization)

The detailed test requirements are outlined below:

- Pre-shipment flash testing for 100% of modules is required with the testing report provided for each individual shipment. The sun simulator must meet the class AAA requirements as specified in IEC 60904-9 standard. The sun simulator must be calibrated with a reference cell, with a maximum uncertainty 1% of Isc. The flash testing report shall contain the unique barcode number with performance parameters (maximum power, short- circuit current, open-circuit voltage, maximum current, maximum voltage) of the module. The flash-test results must be equal or higher than the nameplate rating of the module.

- The barcode shall be on the nameplate of the modules, on the side of the Aluminum frame (if any) and on the front side of the solar module in permanent lasting technology, e.g. laser-engraved.

- A narrow range of module power tolerances is expected. Pre-sorting of solar modules according to IMPP in minimum 3 classes shall be envisaged, with one IMPP-class per container.

- Visual inspection from the same certified PV module testing facility is also required to sample for defects of scratched front surface, misaligned cells, poor labelling and poor sealing.

- All modules must undergo Electroluminescence (EL) inspection with a resolution of minimum 12 MPixel with the testing report provided for each individual shipment. The EL pictures must be in focus. A maximum of 5 minor defects and no major defects per module are allowed.

- EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. The Testing Certificate should be submitted during bidding stage.

- Damp Heat Testing for a duration of minimum 2,000h, certified by an independent 3rd party performed for the selected module type within the last 3 years is a critical selection criterion for the Employer. Testing procedure including certificate is required to be provided during bidding stage.

- Testing in accordance to IEC 60068-2-68 must be provided as a minimum requirement for the modules selected.

- Thermal cycling test for a minimum of 400 cycles in accordance to IEC 61215 is required. The testing certificate shall be provided during bidding stage.

On-Site Testing

The delivered PV modules shall be tested on site to ensure performance during:

- Incoming goods inspection (after shipping):

- Modules site shall undergo visual testing prior to release for installation of the contents of each container with following minimum testing being required.

- Modules shall undergo an incoming inspection of 10 modules per 5 MW for Electroluminescence and PID Testing by an independent testing agency.

- Commissioning and test on completion.

The site tests shall be witnessed by the Employer/Employer’s Engineer. The commissioning test program shall be submitted by the Contractor at least three weeks prior to start of the tests. All relevant costs for the above tests shall be borne by the Contractor.

The Employer expects mature module technology in the PV market with a proven track record in large- scale ground mounted PV installations. References for the module technology are significantly importance. Modules appearing the risk of faster degradation than power output warranty corrosion and de-lamination from electrochemical activity, shall be considered as unfavorable.

The Employer reserves the right to visit the PV module factory at any time during the manufacturing process to verify quality and timely of the production.

Complete documentation shall be provided for the design, manufacturing, testing, commissioning, start-up, operation, maintenance and repair of the DC combiner boxes and their components.

#### Documentation

The Contractor shall provide, as a minimum, the following documentation to be included in the Bid documents:

- Technical datasheets

- Internal layout drawings showing all installed components

- Electrical schematic

- Cable lists

- Spare parts list

- Operation and maintenance manual including component list with manufacturer information e.g. catalogue, etc.

- Yearly PV Module Degradation Table as stated in PVsyst /Detailed Looses/ Ageing

- Reports of tests and commissioning with protocols.

### 2.11.2 Module Mounting Structure

In order to get an optimized design for the PV Plant, the Contractor is free to choose the type of mounting structures and final arrangement on the Site and it shall be confirmed by the employer.

Regardless of the system selected, the Contractor shall consider the following:

- The solar arrays shall be prepared by leveling, compaction and grading. Compaction, improvement or replacement of the soil as determined by the ground investigations shall be carried out to provide the required bearing capacity for all the solar arrays to be deployed and equipment to be installed.

- The foundation design shall be chosen in accordance with Soil Test Report and shall be verified by Contractor's own geotechnical study and ground investigations of the PV Plant area.

- The findings of physical model tests to be carried out to determine the horizontal and uplift loadings likely to be exerted on structure due to highest wind with highest sand content in the area can be considered.

- The mounting structure shall be designed, so that it withstands all of the combined unfavorable loads under consideration of safety factors.

- The solar arrays shall be designed, manufactured and configured in accordance with a commercially proven design in such a way that the conversion of solar irradiation into electricity is based on high efficiency and achieves high availability and reliability.

- The lowest point of PV modules should consider the influence of wave run-up.

- Corrosion protection: Structure connection (nuts, bolts, washers, lock washers, etc.) shall be stainless steel or hot-dip galvanized steel. The Contractor shall take appropriate measures, if necessary, to protect the structure and foundation against corrosion due to salty air, dust and chemical aggressiveness for the expected lifetime of the plant.

- The PV module substructure shall be designed to withstand the continuously repeated washing of the PV modules.

- The Contractor shall demonstrate that his design of the substructure for the PV modules is able to withstand uplift and all weather-induced stress.

- All works shall be planned and done in accordance with the environmental regulations, the impact to the environment during time of construction and the PV Plant use.

- The mounting structure shall be designed in accordance with international and national standards.

- The mounting structure and the foundations shall be designed for a survivability 1 durability of at least 20 years.

- Deconstruction works at the end of lifetime of the PV Plant shall be minimized.

- The structure shall be designed to resist all imposed loads in all possible working conditions. This includes wind load derived from reference wind speed and considering local terrain factors as well as wind gust variations, temperature loads and all other expected live loads.

If a wind barrier shall be installed around the Site the suitability shall be adequately proven by wind channel tests and the design of the barrier needs to be defined in detail including structural verification of the barrier and its foundations. The installation of such system will require the approval of the Employer before start of construction.

Fixed Mounting System

The scope of the PV module fixed mounting system shall comprise at least the following:

- The fixed mounting system shall provide an equally tilted fixed surface of the structures, allowing for an optimized orientation of the PV modules towards the sun.

- The mounting structure shall be adapted to the PV modules manufacturer's requirements with respect to recommended PV module installation of portrait or landscape orientation or long edge or short-edge respectively good accessibility of all module rows to minimize cleaning and maintenance efforts possibility for access of small vehicles between the module rows for mechanical cleaning or other necessary maintenance work. The gap between two module arrays should be equal to more than the height difference of the module array's lower and higher side.

- The PV module mounting frames and structures will be built with fixed tilt angle set in 23º and South orientation. The frames and leg assemble of the array structures shall be made MS hot dip galvanized as per ASTM A123. Minimum thickness of galvanization should be at least 120 microns. All nuts & bolts, Fasteners shall be made of high-quality stainless steel of SS3 04 grade and shall be protected against adverse climatic conditions. The minimum clearance between the lower edge of the modules and the developed ground level shall be 1500 mm and conform to standards.

- The array structure shall be so designed that it will occupy minimum space without sacrificing the output from SPV panels, at the same time it will withstand storm condition with wind speed up to maximum 200 km/h or of wind speed applicable for the zone.

- The structures design shall be appropriate to allow easy replacement of any module, working space for carrying out module cleaning, repairs, replacement, etc. and shall be in line with site requirement. The design of structures should be such that the shade of one structure shall not obstruct the others. The minimum spacing between structures shall be properly maintained and optimized.

- The structures shall be designed with factor of safety of 1.5 or higher as per relevant standards. The array structures shall be grounded properly using Earth Pit.

- The bidder is advised to submit his offer for fixed tracking system of module mounting structures along with guaranteed energy output from the solar system.

### 2.11.3 Grid Tied Inverter (Local Grid)

#### Scope of supply

General

This chapter describes the requirements for the design, manufacturing, installation, testing and commissioning of the inverter to be provided for the project.

The supply shall include all equipment and materials within the scope of work defined in this specification.

Inverter stations shall be built on elevated positions within the project area and shall never be subject to flooding under any circumstance.

The minimum European efficiency of the inverter shall be 97.5% load as per IEC 61683 standard for measuring efficiency. The Contractor should specify the overload capacity of the proposed inverter in the bid.

In order to comply with the guaranteed operational parameters and safety requirements, the Contractor shall provide a complete Plant Design, down to whatever level of detail is necessary, and shall take care of any items that may have not been specified in this Technical Specification.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Contractor.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one and which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

The inverter shall meet all the grid requirements and the operational requirements specified in Bangladeshi Transmission Grid code and the Solar Energy Plants Grid Connection Code. The inverters shall also meet the requirements in IEC 62109-2, and be certified in according to IEC 62116. The inverter shall also be able to control the reactive power or cos φ with an accuracy of +/- 2%.

The Solar Plant shall integrate a synchronization unit (e.g. a phase-locked loop (PLL) or similar) to keep inverters synchronized with the grid before and after being connected to the grid: 1) an inverter can be connected to the grid 2) the inverter can feed the right amount of power to the grid even when the grid voltage changes its frequency, phase, and amplitude.

Inverter shall consist of an electronic inverter along with associated control, protection and data logging devices.

Inverter nominal power shall be minimum 250 kVA.

The rated power/name plate capacity of the inverters shall be the AC output of the inverter at 50˚C.

All Inverter should consist of associated control, protection and data logging devices and remote monitoring hardware and compatible with software used for string level monitoring.

The Inverter shall be tropicalized and design shall be compatible with conditions prevailing at site. Provision of exhaust fan with proper ducting for cooling of Inverter 's should be incorporated in the Inverter's, keeping in mind the extreme climatic condition of the site as per the recommendations of OEM to achieve desired performance and operational life time expectancy.

The inverters shall have minimum protection to IP 66(Outdoor)/IP 21(indoor) and Protection Class II.

The system shall incorporate a unidirectional inverter and should be designed to supply the AC power to the 11-kV bus. The inverter shall adjust the voltage & frequency levels to suit the 11 kV Grid bus.

All three phases shall be supervised with respect to rise/ fall in programmable threshold values of frequency.

Inverter shall confirm to the following standards and appropriately certified by the labs:

- Efficiency measurement:  IEC 61683

- Environmental Testing:   IEC 60068-2 or IEC 62093

- EMC, harmonics, etc.: IEC 61000 series, 6-2, 6-4 and other relevant Standards.

- Electrical safety:  IEC 62109 (1&2), EN 50178 or equivalent

- Recommended practice for PV - Utility interconnections: IEEE standard 929 -2000 or equivalent

- Protection against islanding of grid: IEEE1547/ UL1741/ IEC 62116 or equivalent

- Reliability test standard:   IEC 62093 or equivalent

The Contractor should select the inverters as per its own system design so as to optimize the power output and maximize reliability.

#### General requirements

All the material and works must be in accordance with the most advance practice for this type of equipment. Materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

- DIN / VDE 0126-1-1 Automatic disconnection device between a generator and the public low-voltage grid

- DIN EN 50178 Electronic equipment for use in power installations

- DIN EN 50524 Data sheet and name plate for photovoltaic inverters

- EN 50530 Overall efficiency of photovoltaic inverters

- EN 55022 Information technology equipment. Radio disturbance characteristics. Limits and methods of measurements

- EN IEC 60068 Environmental testing

- IEC 60146-1-1 Semiconductor convertors - General requirements and line- commutated convertors - Part 1-1: Specifications of basic requirements

- IEC 60529 Degrees of protection provided by enclosures

- IEC/EN 61000-3-11 Electromagnetic compatibility (EMC) - Part 3-11: Limits – Limitation of voltage changes, voltage fluctuations and flicker in public low-voltage supply systems - Equipment with rated current ≤ 75 A and subject to conditional connection

- IEC/EN 61000-3-12 Electromagnetic compatibility (EMC) - Part 3-12: Limits – Limit for harmonic currents produced by equipment connected to public low-voltage systems with input current >16 A and ≤ 75 A per phase

- IEC/EN 61000-6-1 Electromagnetic compatibility (EMC) – Part 6-1: Generic standard – Immunity for residential, commercial and light – industrial environments

- IEC/EN 61000-6-2 Electromagnetic compatibility (EMC) - Part 6-2: Generic standards - Immunity standard for industrial environments

- IEC/EN 61000-6-3 Electromagnetic compatibility (EMC) - Part 6-3: Generic standards - Emission standard for residential, commercial and light-industrial environments The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

- EN 61000-6-4 Electromagnetic compatibility (EMC) - Part 6-4: Generic standards - Emission standard for industrial environments

- IEC 61140 Protection against electric shock - Common aspects for installation and equipment

- IEC 61183 Electroacoustics - Random-incidence and diffuse-field calibration of sound level meters

- IEC 61400-21 Harmonics

- IEC 61683 Photovoltaic systems - Power conditioners - Procedure for measuring efficiency

- IEC 61721 Photovoltaic (PV) systems - Characteristics of the utility interface

- IEC 62093 Balance-of-system components for photovoltaic systems - Design qualification natural environments

- IEC/EN 62109-1 Safety of power converters for use in photovoltaic power systems - Part 1: General requirements

- IEC 62109-2 Safety of power converters for use in photovoltaic power systems - Part 2: Particular requirements for inverters

- IEC 62116 Testing procedure of islanding prevention measures for utility interactive photovoltaic inverters

Additionally, all requirements as stated in the Bangladeshi Solar and Grid Code shall be followed.

#### Technical characteristics

The technical characteristics of the inverter are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

#### Design and construction

In addition to the best construction requirements of respective manufacturers, following are the specific requirements for all proposed central inverters:

- Inverters shall be capable of operating at varying power factor in between 0.9 lag to 0.8 lead and shall be able to inject or absorb reactive power.

- Inverters shall be equipped with power islanding prevention system and shall be capable of low and high voltage ride through feature.

- DC and AC Isolation switchgear- All the inverters must be equipped with standard isolation switchgear at the input and output.

- The inverters shall be capable of automatically synchronizing with the grid. All required functions shall be provided in the inverter for safe and reliable auto synchronization.

- Each inverter shall be connected to the grounding system with a cable of adequate diameter. Manufacturer requirements shall be respected by the Contractor.

- According to the module manufacturer requirements the grounding of negative/positive pole shall be provided. The Contractor shall follow the requirements defined by the inverter manufacturer.

- If a positive or negative pole-grounding is required for the proposed module type, the Contractor shall carry out the grounding works to fulfil such requirements. The Contractor shall be responsible to ensure a sufficient ground connection between the strings and the inverter. The Contractor shall be also responsible to ensure the safety disconnection, even for worst case ground conditions, to guarantee the sufficient current required for disconnection. For this issue the Contractor shall demonstrate the complied conditions and qualities by a calculation report submitted for the Employer/Engineer’s approval. A ground fault monitoring, detection and protection system shall be provided and related calculation/details shall be submitted for the Employer/Engineer’s approval.

- The inverter’s Total Harmonics Distortion (THD) shall be below 3%.

- The inverter shall be tested for electromagnetic compatibility in accordance with standards EN 61000-6-2 (interference immunity) and EN 61000-6-4 (interference emission).

- Inverters should be equipped with appropriately designed EMC filters at either ends and sine wave filters at the AC end.

- Inverters shall be equipped with all required hardware for data collection and communication with PSMS. It shall have a facility of direct external communication and control to the Employer. A proven communication protocol such as Profibus, Modbus, Ethernet, or equivalent shall be provided by the Contractor. The selected communication protocol shall be compatible with Plant Control and Monitoring System (PCMS). The inverter shall be able to be controlled by PCMS in order to maintain maximum active power, if required to ensure the grid stability.

- Inverters shall be equipped with appropriately sized forced ventilation system. There shall be redundancy in operation with standby fans.

- Inverters with outdoor duty installation shall have a minimum degree of protection of IP66. Another degree of protection shall be approved by the Employer.

Inverter shall have protection against:

- Over current

- Ground Fault Detector

- Over temperature

- Over voltage

- Reverse current

#### Testing

Factory Acceptance Test (FAT) to be carried out by the manufacturer or manufacturer certified and appointed contractor. The Inverters shall be completely tested in the manufacturers’ workshop in accordance with applicable codes and standards. The tests shall at a minimum include:

- Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed;

- Test run in the field for maximum efficiency of all inverters;

- Test run and check of MPP tracking of all inverters;

- The Contractor shall deliver detailed protocols of the performance test run (warm power test) for every single inverter;

- After commissioning, 5% of inverters (minimum 2 Inverters) shall be measured on site (power curve and efficiency) by an approved independent testing laboratory;

- The on-site measurements shall be accepted by the Contractor as average values for all inverters.

The Inverters shall be tested on site to ensure proper functionality during e.g.

- Visual inspection after delivery on-site

- Thermal Heat Inspection to ensure no overheating

- Pre-commissioning (including “loop testing”)

- Commissioning and test on completion

- Performance tests

- Testing according to IEC 61683

All costs associated with the quality assurance tests of the inverters shall be carried out by the Contractor.

#### Guarantees

The Contractor and manufacturer shall guarantee all the required characteristics. The Contractor shall attend and supervise all the guarantee tests.

The Contractor shall guarantee that the supplied equipment, material, or part thereof shall be in compliance with the specifications hereto and shall be unused products, free from any defects in design, material or workmanship.

A product warranty of minimum ten (10) years shall be provided.

This warranty implies that the Contractor and/or the manufacturer shall repair, or replace if necessary, all the elements damaged during this period.

#### Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Technical datasheets

- Inverter installation manual

- Layout drawings

- Electrical schematic

- Spare parts list and recommended spare part list with equivalent quality to be procured in the country where the site locates

- Operation and maintenance manual

- Reports of tests and commissioning with protocols

- Inverter track record

- Utility grid approval certificate

- Product Warranty

- Suitability Certificate to the site-specific environment

### 2.11.4 Battery Inverter (Smart Inverter) (Usually Named A “Pcs” In A Bess System)

#### Scope of supply

This chapter describes the requirements for the design, manufacturing, installation, testing and commissioning of the Battery Inverter (Smart Inverter) to be provided for the project.

The supply shall include all equipment and materials within the scope of work defined in this specification.

Inverter shall be built on elevated positions within the project area and shall never be subject to flooding under any circumstance.

The minimum European efficiency of the inverter shall be 97.5% load as per IEC 61683 standard for measuring efficiency.

In order to comply with the guaranteed operational parameters and safety requirements, the Contractor shall provide a complete Plant Design, down to whatever level of detail is necessary, and shall take care of any items that may have not been specified in this Technical Specification.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Contractor.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one and which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

The inverters shall also meet the requirements in IEC 62109-2, and be certified in according to IEC 62116. The inverter shall also be able to control the reactive power or cos φ with an accuracy of +/- 2%.

Inverter shall consist of an electronic inverter along with associated control, protection and data logging devices.

Battery Inverter nominal power shall be minimum 200kVA.

The rated power/name plate capacity of the inverters shall be the AC output of the inverter at 50˚C.

All Battery Inverter should consist of associated control, protection and data logging devices and remote monitoring hardware and compatible with software used for string level monitoring.

The Battery Inverter shall be tropicalized and design shall be compatible with conditions prevailing at site. Provision of exhaust fan with proper ducting for cooling of Battery Inverter's should be incorporated in the Battery Inverter's, keeping in mind the extreme climatic condition of the site as per the recommendations of OEM to achieve desired performance and operational life time expectancy.

The inverters shall have minimum protection to IP 66(Outdoor)/IP 21(indoor) and Protection Class II.

The system shall incorporate a bi-directional inverter and should be designed to take AC power from 11 kV bus through 11/LV kV Power Transformer to charge the Battery and supply the AC power at 11kV bus through 11/LV kV Power Transformer. The battery inverter shall adjust the voltage & frequency levels to suit the 11kV bus.

All three phases shall be supervised with respect to rise/ fall in programmable threshold values of frequency.

Battery inverter shall confirm to the following standards and appropriately certified by the labs:

- Efficiency measurement:  IEC 61683

- Environmental Testing:   IEC 60068-2 or IEC 62093

- EMC, harmonics, etc.: IEC 61000 series, 6-2, 6-4 and other relevant Standards.

- Electrical safety:  IEC 62109 (1&2), EN 50178 or equivalent

- Recommended practice for PV - Utility interconnections: IEEE standard 929 -2000 or equivalent

- Protection against islanding of grid: IEEE1547/ UL1741/ IEC 62116 or equivalent

- Reliability test standard:   IEC 62093 or equivalent

The Contractor should select the inverters as per its own system design so as to optimize the power output and maximize reliability.

#### General requirements

All the material and works must be in accordance with the most advance practice for this type of equipment. Materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

- DIN / VDE 0126-1-1 Automatic disconnection device between a generator and the public low-voltage grid

- DIN EN 50178 Electronic equipment for use in power installations

- DIN EN 50524 Data sheet and name plate for photovoltaic inverters

- EN 50530 Overall efficiency of photovoltaic inverters

- EN 55022 Information technology equipment. Radio disturbance characteristics. Limits and methods of measurements

- EN IEC 60068 Environmental testing

- IEC 60146-1-1 Semiconductor convertors - General requirements and line- commutated convertors - Part 1-1: Specifications of basic requirements

- IEC 60529 Degrees of protection provided by enclosures

- IEC/EN 61000-3-11 Electromagnetic compatibility (EMC) - Part 3-11: Limits – Limitation of voltage changes, voltage fluctuations and flicker in public low-voltage supply systems - Equipment with rated current ≤ 75 A and subject to conditional connection

- IEC/EN 61000-3-12 Electromagnetic compatibility (EMC) - Part 3-12: Limits – Limit for harmonic currents produced by equipment connected to public low-voltage systems with input current >16 A and ≤ 75 A per phase

- IEC/EN 61000-6-1 Electromagnetic compatibility (EMC) – Part 6-1: Generic standard – Immunity for residential, commercial and light – industrial environments

- IEC/EN 61000-6-2 Electromagnetic compatibility (EMC) - Part 6-2: Generic standards - Immunity standard for industrial environments

- IEC/EN 61000-6-3 Electromagnetic compatibility (EMC) - Part 6-3: Generic standards - Emission standard for residential, commercial and light-industrial environments The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

- EN 61000-6-4 Electromagnetic compatibility (EMC) - Part 6-4: Generic standards - Emission standard for industrial environments

- IEC 61140 Protection against electric shock - Common aspects for installation and equipment

- IEC 61183 Electroacoustics - Random-incidence and diffuse-field calibration of sound level meters

- IEC 61400-21 Harmonics

- IEC 61683 Photovoltaic systems - Power conditioners - Procedure for measuring efficiency

- IEC 61721 Photovoltaic (PV) systems - Characteristics of the utility interface

- IEC 62093 Balance-of-system components for photovoltaic systems - Design qualification natural environments

- IEC/EN 62109-1 Safety of power converters for use in photovoltaic power systems - Part 1: General requirements

- IEC 62109-2 Safety of power converters for use in photovoltaic power systems - Part 2: Particular requirements for inverters

- IEC 62116 Testing procedure of islanding prevention measures for utility interactive photovoltaic inverters

Additionally, all requirements as stated in the Bangladeshi Solar and Grid Code shall be followed.

#### Technical characteristics

The technical characteristics of the transformer are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

#### Design and construction

In addition to the best construction requirements of respective manufacturers, following are the specific requirements for all proposed inverters:

- Inverters shall be capable of operating at varying power factor in between 0.9 lag to 0.8 lead and shall be able to inject or absorb reactive power.

- Inverters shall be equipped with power islanding prevention system and shall be capable of low and high voltage ride through feature.

- DC and AC Isolation switchgear- All the inverters must be equipped with standard isolation switchgear at the input and output.

- The inverters shall be capable of automatically synchronizing with the grid. All required functions shall be provided in the inverter for safe and reliable auto synchronization.

- Each inverter shall be connected to the grounding system with a cable of adequate diameter. Manufacturer requirements shall be respected by the Contractor.

- According to the module manufacturer requirements the grounding of negative/positive pole shall be provided. The Contractor shall follow the requirements defined by the inverter manufacturer.

- If a positive or negative pole-grounding is required for the proposed module type, the Contractor shall carry out the grounding works to fulfil such requirements. The Contractor shall be responsible to ensure a sufficient ground connection between the strings and the inverter. The Contractor shall be also responsible to ensure the safety disconnection, even for worst case ground conditions, to guarantee the sufficient current required for disconnection. For this issue the Contractor shall demonstrate the complied conditions and qualities by a calculation report submitted for the Employer/Engineer’s approval. A ground fault monitoring, detection and protection system shall be provided and related calculation/details shall be submitted for the Employer/Engineer’s approval.

- The inverter’s Total Harmonics Distortion (THD) shall be below 3%.

- The inverter shall be tested for electromagnetic compatibility in accordance with standards EN 61000-6-2 (interference immunity) and EN 61000-6-4 (interference emission).

- Inverters should be equipped with appropriately designed EMC filters at either ends and sine wave filters at the AC end.

- Inverters shall be equipped with all required hardware for data collection and communication with PCMS system. It shall have a facility of direct external communication and control to the Employer. A proven communication protocol such as Profibus, Modbus, Ethernet, or equivalent shall be provided by the Contractor. The selected communication protocol shall be compatible with Plant Control and Monitoring System (PCMS). The inverter shall be able to be controlled by PCMS in order to maintain maximum active power, if required to ensure the grid stability.

- Inverters shall be equipped with appropriately sized forced ventilation system. There shall be redundancy in operation with standby fans.

- Inverters with outdoor duty installation shall have a minimum degree of protection of IP54. Another degree of protection shall be approved by the Employer.

Inverter shall have protection against:

- Over current

- Ground Fault Detector

- Over temperature

- Over voltage

- Reverse current

#### Testing

Factory Acceptance Test (FAT) to be carried out by the manufacturer or manufacturer certified and appointed contractor. The Inverters shall be completely tested in the manufacturers’ workshop in accordance with applicable codes and standards. The tests shall at a minimum include:

- Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed;

- Test run in the field for maximum efficiency of all inverters;

- Test run and check of MPP tracking of all inverters;

- The Contractor shall deliver detailed protocols of the performance test run (warm power test) for every single inverter;

- After commissioning, 5% of inverters (minimum 2 Inverters) shall be measured on site (power curve and efficiency) by an approved independent testing laboratory;

- The on-site measurements shall be accepted by the Contractor as average values for all inverters.

The Inverters shall be tested on site to ensure proper functionality during e.g.

- Visual inspection after delivery on-site

- Thermal Heat Inspection to ensure no overheating

- Pre-commissioning (including “loop testing”)

- Commissioning and test on completion

- Performance tests

- Testing according to IEC 61683

All costs associated with the quality assurance tests of the inverters shall be carried out by the Contractor.

The site tests shall be witnessed by the Employer/Employer’s Engineer. The commissioning test program shall be submitted at least three (3) weeks prior to the tests.

#### Guarantees

The Contractor and manufacturer shall guarantee all the required characteristics. The Contractor shall attend and supervise all the guarantee tests.

The Contractor shall guarantee that the supplied equipment, material, or part thereof shall follow the specifications hereto and shall be unused products, free from any defects in design, material or workmanship.

A product warranty of minimum ten (10) years shall be provided.

This warranty implies that the Contractor and/or the manufacturer shall repair, or replace if necessary, all the elements damaged during this period.

#### Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Technical datasheets

- Inverter installation manual

- Layout drawings

- Electrical schematic

- Spare parts list and recommended spare part list with equivalent quality to be procured in the country where the site locates

- Operation and maintenance manual

- Reports of tests and commissioning with protocols

- Inverter track record

- Utility grid approval certificate

- Product Warranty

- Suitability Certificate to the site-specific environment

### 2.11.5 Battery Energy Storage System and Battery Management And Pcs

#### General

Battery storage, or battery energy storage systems (BESS), are devices that enable energy from renewables, like solar and wind, to be stored and then released when the power is needed most. Intelligent battery software uses algorithms to coordinate energy production and computerized control systems are used to decide when to store energy or to release it to the grid. Energy is released from the battery storage system during times of peak demand or at night of off grid system. Lithium Iron Phosphate battery (LiFePO4 battery) or LFP battery (lithium ferro phosphate) technologies shall be used as an energy storage device which fulfill the performance parameters presented in below chapters.

#### Codes and Standards

All the material and works must be in accordance with the most advance practice for this type of equipment. All the materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

- IEC 62619:2022 Secondary cells and batteries containing alkaline or other non-acid electrolytes - Safety requirements for secondary lithium cells and batteries, for use in industrial applications

- UL 62109-1 “Safety of power converters for use in photovoltaic power systems – Part 1: General requirements.”

- BESS inverter shall meet IEEE 1547-2018 standards for grid-tied operation

- UL 1741 – Inverters, Converters, Controllers and Interconnection System Equipment for Use with Distributed Energy Resources

- UL 1741SA – Supplemental testing for advanced grid inverters

- IEEE 1547-2018 – Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces

- IEEE 519 – Recommended Practice and Requirements for Harmonic Control in Electric Power Systems

- UL 9540 “Energy Storage Systems and Equipment”

- UL 1642 “Standard for Lithium Batteries.”

- UL 9540 “Energy Storage Systems and Equipment”

- UL 9540A “Test Method for Evaluating Thermal Runaway Fire Propagation in Battery Energy Storage Systems.”

- ANSI C84.1 – Electric Power Systems and Equipment – Voltage Ranges

- NFPA 1 – Fire Code

- NFPA 70 – National Electric Code

- NFPA 855 – Standard for the Installation of Stationary Energy Storage Systems, 2020 edition

Battery Energy Storage

Lithium-ion batteries, which are used in mobile phones and electric cars, are currently the dominant storage technology for large scale plants to help electricity grids ensure a reliable supply of renewable energy. The lithium iron phosphate battery (LiFePO4 battery) or LFP battery (lithium ferro phosphate) shall be used as an energy storage device.

The main feature of Battery Energy Storage:

- The BESS shall be containerized, using either standard International Organization for Standardization (ISO) 668 shipping containers or custom-designed power equipment centers.

- The container or containers shall be designed to be drop-shipped onto a properly prepared pad or foundation (such as compacted soil, concrete pad or platform, and so on).

- When fully installed in factory, all BESS components—including battery racks all auxiliaries, such as HVAC and fire suppression systems, step-up transformers to match grid, ac switchgear, and so on—and tools shall be enclosed in (or on) the containers, even if certain components must be separately shipped and installed at the site.

- Battery pack and battery rack shall be pre-installed.

- The design and installation of Containers shall meet relevant regulatory requirements for occupational safety and health under national and state legislations.

- Containers shall be non-walk-in battery container.

- HVAC shall be distributed and each battery cluster shall be configured with an independent air conditioner.

- BESS shall have pack level optimization function which means each battery pack should have a pack optimizer, which is in parallel with battery pack.

- BESS shall have rack level optimization function which means each battery rack should have a rack controller, which is in series with the battery rack.

- Container electrical system security: Battery modules and battery clusters shall be configured with active protection and refined charging and discharging management functions to prevent thermal runaway caused by overcharge and over discharge of packs and battery racks. The rack manager electrically isolates each battery rack to avoid thermal runaway due to excessive circulating current in parallel.

- Electrical networking security: The electrical networking system from the battery compartment to the PCS shall uses a dual-level electrical system architecture consisting of a DC/DC converter and a DC/AC bidirectional converter. The DC/DC converter isolates batteries from power grid faults. Avoid thermal runaway caused by external electrical factors such as power grid faults and high voltage pass-through.

- Energy storage and fire extinguishing system shall configure flammable gas detector, fire detector, clean gas extinguishing device, combustible gas discharge device, intelligent detection. The battery prefabricated compartment shall be equipped with an automatic fire extinguishing system, fire alarm, and linkage control system, and the energy storage compartment is equipped with an automatic fire extinguishing system. Water detection and linkage protection function shall be configured; when water flood occur, the power circuit is cut off in time to avoid electric shock, high voltage short circuit, and short circuit spread.

- The fire protection design of container shall have a combustible composite gas detection system. The combustible gas detector can detect the concentration of combustible gases such as H2 and CO. When any combustible gas detector generates an alarm, the exhaust controller starts and controls the exhaust fan to remove the gas in the container from the exhaust module until the detected concentration of the combustible gas detector is lower than the start value.

- The battery compartment, environment control, power distribution, and fire extinguishing compartments must be designed separately to ensure that the monitoring and fire extinguishing system can operate independently and continuously when an exception occurs in the battery compartment.

- The EPO function enables you to manually and quickly cut off the main circuit of the ESU in case of a short circuit, electric shock, or fire, preventing accidents from spreading.

- BESS shall have Integrated modular high-efficiency redundant liquid-cooling system, with the temperature difference in the container limited to 5℃.

- The BESS shall have resistance up to C5 corrosion level, with 20-year reliability.

- Protection level: IP 55 (Outdoor application)

- BESS needs to be certified according to UL9540A or equivalent

Battery Management System (BMS)

- The monitoring, controlling and configuration of all input and output logical signals and binary inputs and relay outputs for all built-in functions and signals shall be possible both locally and remotely.

- The BMS shall be configured to have automatic control to ensure the balance between cells/modules/racks (where applicable) to ensure optimized state of charge (SOC), state of health (SOH) and life expectancy. Avoid capacity loss and circulation risks caused by inconsistency. The BMS shall have automatic SOC calibration function instead of engineer site visit to calibrate SOC.

- The BMS shall be designed as multi-level architecture.

- Battery management unit: shall be able to monitor and collect battery running information, manage cell passive balancing, diagnose faults, and control battery pack switch-out using the battery pack optimizer.

- Battery control unit: shall be able to collect information about all battery packs, and collect the voltage and current of the entire rack. Alarms and protection are provided for abnormal battery packs during the charging and discharging of the battery packs. In addition, by issuing a control command to the Battery management unit, the Battery management unit performs current equalization control among battery packs in the rack, and switches out each battery pack independently to achieve optimization.

- Container management unit: shall be able to manages the battery management unit and battery control unit, analyze and calculate the uploaded data, process alarms, record and store the data, manage the balance between racks, and manage SOC and SOH. At the same time, the environment controller collects data from the container environment monitoring system. (fire extinguishing system, temperature control system, temperature and humidity sensor, and water sensor) Information: Formulate proper temperature control policies to improve battery temperature consistency and implement comprehensive fire warning, protection, and linkage for the energy storage system to provide highly reliable fire safety assurance, and implement effective prevention, early detection, and effective isolation and protection.

- Array control unit: shall be able to collect the data from containers and upload to EMS, receive power grid scheduling commands and deliver them to the PCS and container control unit to meet power grid scheduling requirements.

Analog data and Digital status data (reported by exception) shall be updated and displayed at the control center in real time. An integrity scan of all analog/ digital data shall also be made regularly and any discrepancies between field status and database shall be reported by an alarm message. Monitoring & Control system shall monitor & display at least following parameters in Energy management system.

- Operation Mode (Grid connected mode / Standalone mode /Manual / Automatic charging / Discharging)

- Application Mode (Ramping Control/Energy time-shift/Power Firming)

- Measurements (V, I, P, Q, f, Energy Export / Import)

- Events i). Alarms ii) Breaker position/operation

- Parameters of power conditioning system & power management system f) visualized status of health of each battery

- Estimated time for charging

- Estimated discharge time at ongoing discharge rate

- Fault information

- Protection operation information

- Alarms for over charge, over discharge, over current, over voltage, high temperature, protection operation etc.

- Energy Efficiency of PCS

- Status of air-conditioning system

- Status of fire protection system

- Ambient temperature xviii. Trending of parameters

- Battery Cycles: Utilized Cycles and Un-utilized Cycle.

- Fault with HVAC Systems alarm

- Container Door Open alarm

- Smoke/Fire alarm.

Tests

A comprehensive FAT has to be conducted and witnessed by the Employer/Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests 30 days, a test procedure shall be submitted to the Employer/Employer’s Engineer for the approval. A full protocol and test results shall be submitted to the Employer’s Engineer after the testing.

Guarantee

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall be in compliance with the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts (spare parts are quoted as optional).

The warranty period must be two (2) years and it shall begin from the Operational acceptance. This warranty implies that the Supplier and the Contractor shall repair, or replace, if necessary, all the elements damaged during this period.

This warranty implies that the Supplier shall repair, or replace if necessary, all the elements damaged during this period.

Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- A site plan showing the BESS footprint

- Electrical schematic diagrams (interconnection, system one-line diagrams)

- Useable energy storage capacity (kWh)

- Rated power (kW AC)

- AC:AC efficiency (including auxiliary loads)

- Cycle life

- Annual degradation factor

- Ambient temperature control system

- Fire protection/suppression system description as required by code

- Maintenance requirements

- Confirmation that the proposed system can integrate with existing solar photovoltaics, if applicable

- BESS-specific sequences of operation should be included for all modes of operation and use cases.

Energy Management System (EMS)

The purpose of the Energy Management System (EMS) is to issue schedule, dispatch, and operating mode instructions to the electricity generating subsystems (solar PV plant, and BESS). The instructions must ensure that system safety requirements, reliability, and power quality requirements are maintained, while minimizing use of fuel (diesel), minimizing generator run-time and starts and also seamlessly initiate black start in case of such occurrence.

The EMS must:

- Operate proven and configurable algorithms demonstrating reliable operation of hybrid energy systems of a similar scale, and providing for optimal dispatch of solar PV, BESS, and diesel generation to minimize cost of energy. Capabilities should include:

  - Ability to control BESS and solar PV plant under all their intended control modes.

  - User configurable (tunable) settings for inputs to dynamic spinning reserve calculation, ramp times, delays, limits, and conditions for state transition under varying load.

- Be operable as a stand-alone system, even when the BESS or solar PV is off-line for maintenance.

- Be separable, such that the existing thermal power plant can continue to operate if the EMS is off-line.

- Use Modbus TCP communications and fiber optic connections

- Be capable of integrating with diesel generator controllers,

- Be capable of interfacing with solar PV plant with SunSpec protocols, and associated switchgear

- Be capable of interfacing with other subsystems of the plant

- Be capable of interfacing with remote equipment via optic fiber or 4G communications

- Be capable of interfacing with other BESS and micro-grid controllers that may be installed later for capacity expansion, operating in the network (subject to above expectations on interface and communications, and cooperation of the supplier / operator of that equipment); may require definition of a response profile for management of that other equipment

- Include an HMI, with remote web access capability, also accessible on the power station operator workstation

- Provide expansion capability to add or reconfigure BESS, solar PV, or thermal generators over the EMS life

- The EMS must provide flexibility for future upgrade requirements. Future upgrade requirements may include addition of new generators/BESS/PV Plant or configuration changes in the network, or adopting improvements in available EMS software. EMS vendor will be required to offer product support and support for such requirements (which may include remote support and site visits if needed). EMS vendor will be required to provide fully documented open source code on standard industrial hardware, or other provision to ensure the EMS is not stranded / left unsupported under any circumstance.

- The EMS should also support (prevent disruption of) operations that do not require the BESS and solar PV plant, including black start (ensuring compatible setting of solar PV and BESS state, mode, or other requirement, including their respective switchgear, and communicating status with the thermal system)

- The EMS shall be configurable to operate in a zero-diesel scenario (100% renewables), despite not being the expected normal operation mode.

- Open source code for all software shall be utilized wherever this option is available. Open source code shall be provided as a deliverable, including documentation.

### 2.11.6 Power Transformer

A transformer is a static device that transfers electrical energy from one electrical circuit to another circuit, or multiple circuits without changing the frequency. It is mainly used to increase or decrease the voltage level between the generator and the distribution circuits. In this project power transformer of different capacity will used to step up the voltage.

- LV/11 kV Power Transformer (for BESS to MV and PV to MV)

- 0.4/11kV Power Transformer (for diesel generator)

- 11/0.4 kV Auxiliary Transformer (for UPS)

LV/11 kV Power Transformer (for BESS to MV and PV to MV)

General

The transformers shall be designed to be highly efficient and provide a reliable performance under the defined system and climatic conditions. The supply shall include all equipment and materials within the battery limits defined in this specification.

In order to comply with the guaranteed operational parameters and safety requirements, the Contractor shall provide a complete Plant Design, down to whatever level of detail is necessary, and shall take care of any items that may have not been specified in this Technical Specification. The equipment to be supplied shall also be designed so that all provisions for easy inspection, cleaning, maintenance and repair.

The Contractor shall take care that all necessary components for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for a proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is integrated into the overall plant concept. The scope of supply shall include all components required to ensure a safe and proper operation as well as the maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications and environments (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to the good practice.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which of the compulsory requirement is finally applied.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Transformers must be outdoor type with an adequate IP protection in accordance with the environmental conditions.

Equipment and components

- Transformers of 11kV±2.5% ±5%/LV, Dyn11, 50 Hz. Resin encapsulated

- Transformer minimum Capacity 3400 kVA,

- Any other description could be considered according to final lay-out proposed by the Contractor but is shall be accepted by the Employer.

General requirements

- All the material and works must be in accordance with the most advance practice for this type of equipment. All the materials and realized works shall be in accordance with latest

- of the IEC recommendations.

- The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards: International Electrotechnical Commission (IEC).

- The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

The transformers shall be designed, manufactured and tested according to the following Standards:

- IEC 60044	Instrument transformers.

- IEC 60060	High voltage test techniques.

- IEC 60071	Insulation co-ordination.

- IEC 60076	Power transformers.

- IEC 60137	Bushings for alternating voltages above 1000 V.

- IEC 60233	Test on hollow insulators for use in electrical equipment.

- IEC 60551	Determination of transformer and reactor sound level.

- IEC 60722	Guide to the lightning impulse and switching impulse testing.

- IEC 60038	Nominal Voltages.

- IEC 60354	Charge Guide to power transformers inside oil refrigeration.

- IEC 60551	Noise level detection in transformers and reactance.

- IEC 60156	Method to determine electrical perforation voltage of insulating oils.

- IEC 60296	Fluids for electro technical applications. Requirements for new insulating mineral oils for transformers and switchgear.

- IEC 60616	Marking shots terminals and power transformers.

- IEC 60772	Application Guide in trials and type lightning impulse maneuver for power transformers and reactors.

Any other International Standard mentioned during the present document shall be used also to design, manufacture and/or test.

Additionally, all requirements as stated in the Bangladeshi Solar and Grid Code shall be followed.

4. Technical characteristics

The technical characteristics of the transformers are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

- Design and construction

General

- The transformers shall be ready to operate continuously outdoor.

- Auxiliary Control devices (Buchholz, thermometer, thermostats, levels, etc.) shall be wired to a junction box with protection degree IP-65.

- The transformers shall be designed for a continuous operation on the nominal load, without surpassing the warming-up levels.

- The transformers shall have independent windings for the primary and two secondary circuits. The material for the windings shall be copper.

- The primary terminals shall be permanently marked U, V and W and the secondary terminals u, v and w.

- All material used shall be of best quality and of the class most suitable for working under the conditions as specified.

- The material shall withstand the variations of temperature, atmospheric conditions, overloads, over excitation and short circuits as per standards without distortion, deterioration and the setting-up of undue stresses in any part.

- The supplied transformers shall be identical and their parts shall be interchangeable.

- Nuts, bolts and pins shall be provided with lock washers or locknuts.

- Nominal rated power shall be determined in natural circulation cooled and self-cooled oil natural air ventilation (ONAN type).

- All power transformers shall be open type, with expansion tank and radiators. They shall be prepared to increase, if necessary, its nominal power (kVA) and to provide extra cooling in case it is needed by incorporating fans for forced cooling ONAF type.

- All elements of the transformer (windings, connections, terminals, etc.) shall be electrically and mechanically dimensioned for nominal values of the output rated power that corresponds to the use of fans, refrigeration ONAF.

- Expressed as a percentage relative power with ONAN cooling, transformers may increase (at least) with the use of cooling fans ONAF, 10% more power.

- Unless otherwise specified in the requisition, the transformers shall be built for installation in safe areas without risk of fire or explosion.

- Load losses and short-circuit and the load current shall be indicated on the requisition of material.

- Regarding tolerances shall apply the rates specified in IEC 60076-1.

- Load losses and load current shall be referred to the nominal frequency. Load losses and impedance voltage are referred to the center tap of the switch or regulator, a nominal frequency and temperature of 75°C. Short-circuit voltage is always related to the power in ONAN regime.

- Load or vacuum switches (voltage) shall be particularly resistant to transient overload and short circuit currents, minimum dimensioned for 110% intensity ONAF cooled transformer in the event that this can be implemented, taking into also has the most unfavorable position of the switch.

Core

- Transformer design shall be core type.

- The core shall be made out of high-grade low loss cold-rolled non-ageing grain oriented or equivalent.

- The yoke laminations shall be interleaved and carefully assembled to avoid air-gaps in the magnetic circuit. All Core sections shall be earthed as per the relevant standards.

- The insulation structure in between core to bolts and core to clamp plates shall withstand a minimum voltage of 2,500 V for one minute.

- All steel sections used for supporting the core shall be non-magnetic and thoroughly shot or sand blasted, after cutting, drilling, welding, etc.

- The design of the magnetic circuit shall be such as to avoid static discharges, development of short circuit paths within itself or to the earthed clamping structure.

- The assembled core with all the clamping structures shall be free from deformation and shall withstand the vibrations during operation.

- The core clamping structure shall be designed to minimize eddy current losses.

- This shall be made from laminations of grain-oriented silicon steel, insulated with mineral oxide and shall be protected against corrosion with a coat of varnish.

- In order to reduce the power consumption due to transformer no-load losses, the magnetic core is stacked using overlapping-interlocking technology, with at least 6 overlaps.

Windings.

- The design and arrangement of the windings and their insulation shall be such as to ensure uniform distribution of the voltage surges among all the coils of the windings.

- The insulation shall have high tensile and dielectric strength. Enough measures shall be taken during casting of the windings to avoid cracking & crazing of the casted coils.

- The transformer shall be able to withstand short circuits as well as switching and lightning/atmospheric impulse voltages. The leads and connections shall be mechanically strong and adequately brazed to withstand short circuit forces and transportation shocks.

Earthing.

Single point earthing shall be used for magnetic circuit. The frame work and clamping arrangements of core and coil shall be securely earthed by copper strip connection to the main frame and enclosure.

Earthing of the primary side of the transformer shall be according to the requirements of the Bangladesh Electricity Grid Code, 2018.

Oil

Characteristics of the oil, before filling the transformer, shall be according for uninhibited oils without synthetic product mixtures, Class II according to IEC-60296.

Oil filling shall be done under vacuum to obtain a dielectric strength, according to IEC-60156.

Limit values of transformer oil extracted before submission to load, shall be as shown in the following table:

| Characteristics | Limit | Essay method |
| --- | --- | --- |
| Water content (mg/kg) | 20 as maximum | IEC-60296 |
| Neutralization # (mg KOH/g) | 0.03 as maximum | IEC-61125 |
| Interphase Stress (N/m 10-3) | 30 as minimum | IEC-60296 |
| Dielectric’s losses factor at 90º(tg) | 0.015 as maximum | IEC-60247 |
| Dielectric’s rupture voltage (kV) | 40 as minimum | IEC-60296 |

Casing and radiators

- Casing and covers shall be resistant to vacuum without causing permanent deformation.

- The cover shall be flat. The reinforcements have at the top to the free movement of gas bubbles to the Buchholz relay in the case of transformers with conservator tank. All sealings shall be of neoprene or other material permanently insulating liquid and oil resistant.

- Both, casing and radiators, must be made of steel sheet; shall be hot dip galvanized and shall be so arranged as to facilitate the cleaning and painting.

- All transformers must be provided with steerable wheels in both directions of the main axes and arranged at the bottom of casing, and with supports for lifting by means of jacks.

- Radiators in oil transformers shall be isolated of casing by valves.

Expansion tank.

- The connecting line between casing and the expansion tank shall start from the highest point of the casing and inserted into the bottom of the tank.

- The expansion tank shall be provided with tight filling plug at the top and a drain at the bottom, both of them will be standard.

- On one side, the expansion tank shall have a magnetic type level indicator with readout filling at 20°C, and indications of minimum and maximum level. It will have two, potential-free normally-open electrical contacts, one for alarm and one for trip; the opposite side shall be prepared to accept a second level indicator.

- The expansion tank shall have a vent fitted with silica gel desiccant breather.

- To prevent over pressurization, the expansion tank will be equipped with an automatic pressure relief valve.

MV connections.

- The MV side termination facility of the transformers shall be designed for connecting 11 kV XLPE up to 500mm2 insulated cable terminated in crimping type lugs and heat shrinkable sleeves or pre-molded cast resin push on type terminations.

- Each connection bar shall be drilled for connection of cable lugs on terminal plates.

- The MV connection bars shall be in rigid copper bars protected by heat shrinkable tubing.

- MV bushing terminals shall be extended up to the cable terminals and the bus bars shall be located at a convenient height.

- The MV cable entry shall be from the bottom of the metal enclosure.

- The winding delta formation on MV side shall be in supplier’s scope.

Bushing.

- The design of the bushings shall be carried out considering the current corresponding to the transformer power.

- The specific length of the vanishing line´s terminals must be not less than 2.5 cm/kV maximum operating voltage.

- The bushings shall be made of best quality vitrified porcelain and shall comply with the relevant regulations.

- The joining shall be tight against air, isolating liquid and water, and resistant to ambient conditions.

- The bushings for the aerial connections shall be provided with adjustable antenna dischargers, in accordance with what is indicated as regards this matter.

Temperature sensor & transformer protection

- Oil temperature sensors, temperature indication device as well as oil temperature warning and alarm contacts shall be provided for each transformer.

- Buchholz relay shall be provided for transformer protection with warning and alarm contacts.

Fittings and accessories

Following fittings and accessories shall be provided:

- Rating, terminal marking and danger plates.

- Three earth terminals per transformer.

- Separate lugs for lifting complete transformer (Core & Coil assembly) and for enclosure

- Four bi-directional rollers in base frame with stopper arrangement to lock the transformer in the required position.

- Neutral earth terminal with lugs.

- Six number PT100 with a WTI display.

- Oil temperature measurement and indication.

Off-load Tap changer.

- The Contractor has to provide a tap changer design that is suitable for any possible operation condition of the Plant.

- The handling of the tap changer shall be independent from the tank, to avoid gas or isolating liquid leakage, and shall be provided with appropriate protections.

Testing

A comprehensive FAT (tests according to IEC 60076) has to be conducted and witnessed by the Employer/Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests 30 days, a test procedure shall be submitted to the Employer/Employer’s Engineer for the approval. A full protocol and test results shall be submitted to the Employer’s Engineer after the testing.

Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall be in compliance with the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts.

The warranty period must be two (2) years and it shall begin from the Operational acceptance.

This warranty implies that the Supplier and the Contractor shall repair, or replace if necessary, all the elements damaged during this period.

Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Technical data sheets

- Transformer layout drawings showing all installed components

- Electrical schematic

- Warranty

- Spare parts list

- Operation and maintenance manual including component list with manufacturer information e.g. catalogue, etc.

- Reports of tests and commissioning with protocols Tests

2.11.6.1 0.4/11kv Power Transformer

General

The transformers shall be designed to be highly efficient and provide a reliable performance under the defined system and climatic conditions. The supply shall include all equipment and materials within the battery limits defined in this specification.

In order to comply with the guaranteed operational parameters and safety requirements, the Contractor shall provide a complete Plant Design, down to whatever level of detail is necessary, and shall take care of any items that may have not been specified in this Technical Specification. The equipment to be supplied shall also be designed so that all provisions for easy inspection, cleaning, maintenance and repair.

The Contractor shall take care that all necessary components for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for a proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is integrated into the overall plant concept. The scope of supply shall include all components required to ensure a safe and proper operation as well as the maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications and environments (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to the good practice.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which of the compulsory requirement is finally applied.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Transformers must be outdoor type with an adequate IP protection in accordance with the environmental conditions.

Equipment and components.

Transformers of 0.4/11kV±2.5% ±5%, Dyn11, 50 Hz. Resin encapsulated

Transformer minimum Capacity 1250 kVA,

Any other description could be considered according to final lay-out proposed by the Contractor but is shall be accepted by the Employer.

General requirements

All the material and works must be in accordance with the most advance practice for this type of equipment. All the materials and realized works shall be in accordance with latest  of the IEC recommendations.

- The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards: International Electrotechnical Commission (IEC).

- The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

- The transformers shall be designed, manufactured and tested according to the following Standards:

- IEC 60044	Instrument transformers.

- IEC 60060	High voltage test techniques.

- IEC 60071	Insulation co-ordination.

- IEC 60076	Power transformers.

- IEC 60137	Bushings for alternating voltages above 1000 V.

- IEC 60233	Test on hollow insulators for use in electrical equipment.

- IEC 60551	Determination of transformer and reactor sound level.

- IEC 60722	Guide to the lightning impulse and switching impulse testing.

- IEC 60038	Nominal Voltages.

- IEC 60354	Charge Guide to power transformers inside oil refrigeration.

- IEC 60551	Noise level detection in transformers and reactance.

- IEC 60156	Method to determine electrical perforation voltage of insulating oils.

- IEC 60296	Fluids for electro technical applications. Requirements for new insulating mineral oils for transformers and switchgear.

- IEC 60616	Marking shots terminals and power transformers.

- IEC 60772	Application Guide in trials and type lightning impulse maneuver for power transformers and reactors.

Any other International Standard mentioned during the present document shall be used also to design, manufacture and/or test.

Additionally, all requirements as stated in the Bangladeshi Solar and Grid Code shall be followed.

Technical characteristics

The technical characteristics of the transformers are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

Design and construction

General

- The transformers shall be ready to operate continuously outdoor.

- Auxiliary Control devices (Buchholz, thermometer, thermostats, levels, etc.) shall be wired to a junction box with protection degree IP-65.

- The transformers shall be designed for a continuous operation on the nominal load, without surpassing the warming-up levels.

- The transformers shall have independent windings for the primary and two secondary circuits. The material for the windings shall be copper.

- The primary terminals shall be permanently marked U, V and W and the secondary terminals u, v and w.

- All material used shall be of best quality and of the class most suitable for working under the conditions as specified.

- The material shall withstand the variations of temperature, atmospheric conditions, overloads, over excitation and short circuits as per standards without distortion, deterioration and the setting-up of undue stresses in any part.

- The supplied transformers shall be identical and their parts shall be interchangeable.

- Nuts, bolts and pins shall be provided with lock washers or locknuts.

- Nominal rated power shall be determined in natural circulation cooled and self-cooled oil natural air ventilation (ONAN type).

- All power transformers shall be open type, with expansion tank and radiators. They shall be prepared to increase, if necessary, its nominal power (kVA) and to provide extra cooling in case it is needed by incorporating fans for forced cooling ONAF type.

- All elements of the transformer (windings, connections, terminals, etc.) shall be electrically and mechanically dimensioned for nominal values of the output rated power that corresponds to the use of fans, refrigeration ONAF.

- Expressed as a percentage relative power with ONAN cooling, transformers may increase (at least) with the use of cooling fans ONAF, 10% more power.

- Unless otherwise specified in the requisition, the transformers shall be built for installation in safe areas without risk of fire or explosion.

- Load losses and short-circuit and the load current shall be indicated on the requisition of material.

- Regarding tolerances shall apply the rates specified in IEC 60076-1.

- Load losses and load current shall be referred to the nominal frequency. Load losses and impedance voltage are referred to the center tap of the switch or regulator, a nominal frequency and temperature of 75°C. Short-circuit voltage is always related to the power in ONAN regime.

- Load or vacuum switches (voltage) shall be particularly resistant to transient overload and short circuit currents, minimum dimensioned for 110% intensity ONAF cooled transformer in the event that this can be implemented, taking into also has the most unfavorable position of the switch.

Core

- Transformer design shall be core type.

- The core shall be made out of high-grade low loss commi-rolled non-ageing grain oriented or equivalent.

- The yoke laminations shall be interleaved and carefully assembled to avoid air-gaps in the magnetic circuit. All Core sections shall be earthed as per the relevant standards.

- The insulation structure in between core to bolts and core to clamp plates shall withstand a minimum voltage of 2,500 V for one minute.

- All steel sections used for supporting the core shall be non-magnetic and thoroughly shot or sand blasted, after cutting, drilling, welding, etc.

- The design of the magnetic circuit shall be such as to avoid static discharges, development of short circuit paths within itself or to the earthed clamping structure.

- The assembled core with all the clamping structures shall be free from deformation and shall withstand the vibrations during operation.

- The core clamping structure shall be designed to minimize eddy current losses.

- This shall be made from laminations of grain-oriented silicon steel, insulated with mineral oxide and shall be protected against corrosion with a coat of varnish.

- In order to reduce the power consumption due to transformer no-load losses, the magnetic core is stacked using overlapping-interlocking technology, with at least 6 overlaps.

Windings.

- The design and arrangement of the windings and their insulation shall be such as to ensure uniform distribution of the voltage surges among all the coils of the windings.

- The insulation shall have high tensile and dielectric strength. Enough measures shall be taken during casting of the windings to avoid cracking & crazing of the casted coils.

- The transformer shall be able to withstand short circuits as well as switching and lightning/atmospheric impulse voltages. The leads and connections shall be mechanically strong and adequately brazed to withstand short circuit forces and transportation shocks.

Earthing.

Single point earthing shall be used for magnetic circuit. The frame work and clamping arrangements of core and coil shall be securely earthed by copper strip connection to the main frame and enclosure.

Earthing of the primary side of the transformer shall be according to the requirements of the Bangladesh Electricity Grid Code, 2018.

Oil.

Characteristics of the oil, before filling the transformer, shall be according for uninhibited oils without synthetic product mixtures, Class II according to IEC-60296.

Oil filling shall be done under vacuum to obtain a dielectric strength, according to IEC-60156.

Limit values of transformer oil extracted before submission to load, shall be as shown in the following table:

| Characteristics | Limit | Essay method |
| --- | --- | --- |
| Water content (mg/kg) | 20 as maximum | IEC-60296 |
| Neutralization # (mg KOH/g) | 0.03 as maximum | IEC-61125 |
| Interphase Stress (N/m 10-3) | 30 as minimum | IEC-60296 |
| Dielectric’s losses factor at 90º(tg) | 0.015 as maximum | IEC-60247 |
| Dielectric’s rupture voltage (kV) | 40 as minimum | IEC-60296 |

Casing and radiators

- Casing and covers shall be resistant to vacuum without causing permanent deformation.

- The cover shall be flat. The reinforcements have at the top to the free movement of gas bubbles to the Buchholz relay in the case of transformers with conservator tank. All sealings shall be of neoprene or other material permanently insulating liquid and oil resistant.

- Both, casing and radiators, must be made of steel sheet; shall be hot dip galvanized and shall be so arranged as to facilitate the cleaning and painting.

- All transformers must be provided with steerable wheels in both directions of the main axes and arranged at the bottom of casing, and with supports for lifting by means of jacks.

- Radiators in oil transformers shall be isolated of casing by valves.

Expansion tank.

- The connecting line between casing and the expansion tank shall start from the highest point of the casing and inserted into the bottom of the tank.

- The expansion tank shall be provided with tight filling plug at the top and a drain at the bottom, both of them will be standard.

- On one side, the expansion tank shall have a magnetic type level indicator with readout filling at 20°C, and indications of minimum and maximum level. It will have two, potential-free normally-open electrical contacts, one for alarm and one for trip; the opposite side shall be prepared to accept a second level indicator.

- The expansion tank shall have a vent fitted with silica gel desiccant breather.

- To prevent over pressurization, the expansion tank will be equipped with an automatic pressure relief valve.

MV connections.

- The MV side termination facility of the transformers shall be designed for connecting 11 kV XLPE up to 500mm2 insulated cable terminated in crimping type lugs and heat shrinkable sleeves or pre-molded cast resin push on type terminations.

- Each connection bar shall be drilled for connection of cable lugs on terminal plates.

- The MV connection bars shall be in rigid copper bars protected by heat shrinkable tubing.

- MV bushing terminals shall be extended up to the cable terminals and the bus bars shall be located at a convenient height.

- The MV cable entry shall be from the bottom of the metal enclosure.

- The winding delta formation on MV side shall be in supplier’s scope.

Bushing.

- The design of the bushings shall be carried out considering the current corresponding to the transformer power.

- The specific length of the vanishing line´s terminals must be not less than 2.5 cm/kV maximum operating voltage.

- The bushings shall be made of best quality vitrified porcelain and shall comply with the relevant regulations.

- The joining shall be tight against air, isolating liquid and water, and resistant to ambient conditions.

- The bushings for the aerial connections shall be provided with adjustable antenna dischargers, in accordance with what is indicated as regards this matter.

Temperature sensor & transformer protection.

- Oil temperature sensors, temperature indication device as well as oil temperature warning and alarm contacts shall be provided for each transformer.

- Buchholz relay shall be provided for transformer protection with warning and alarm contacts.

Fittings and accessories

Following fittings and accessories shall be provided:

- Rating, terminal marking and danger plates.

- Three earth terminals per transformer.

- Separate lugs for lifting complete transformer (Core & Coil assembly) and for enclosure

- Four bi-directional rollers in base frame with stopper arrangement to lock the transformer in the required position.

- Neutral earth terminal with lugs.

- Six number PT100 with a WTI display.

- Oil temperature measurement and indication.

Off-load Tap changer.

- The Contractor has to provide a tap changer design that is suitable for any possible operation condition of the Plant.

- The handling of the tap changer shall be independent from the tank, to avoid gas or isolating liquid leakage, and shall be provided with appropriate protections.

Testing

A comprehensive FAT (tests according to IEC 60076) has to be conducted and witnessed by the Employer/Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests 30 days, a test procedure shall be submitted to the Employer/Employer’s Engineer for the approval. A full protocol and test results shall be submitted to the Employer’s Engineer after the testing.

Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall follow the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts.

The warranty period must be two (2) years and it shall begin from the Operational acceptance.

This warranty implies that the Supplier and the Contractor shall repair, or replace if necessary, all the elements damaged during this period.

Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Technical data sheets

- Transformer layout drawings showing all installed components

- Electrical schematic

- Warranty

- Spare parts list

- Operation and maintenance manual including component list with manufacturer information e.g. catalogue, etc.

- Reports of tests and commissioning with protocols Tests

2.11.6.2 11/0.4 Kv Auxiliary Transformer

Auxiliary Transformer shall be rated based on the rating of the loads it has to supply. The Contractor shall submit detail design of auxiliary system. For the dry-type transformers the temperature rise shall not be exceed 90℃.

All component and accessory parts must be constructed using carefully selected materials and be of appropriate design to match the service life of the transformer. The manufacturer will be responsible for the selection of all materials used in the transformer.

The auxiliary transformers shall also be designed for the ambient conditions on site. Bidder shall provide with its proposal a diagram showing the capacities of the auxiliary transformer versus the ambient temperature on site.

2.11.7 LV/MV SWITCHGEAR

Low Voltage (LV) and Medium Voltage (MV) switchgear shall be designed to be highly efficient and provide a reliable system operation in accordance with the internationally proven standard system and existing climatic conditions of Bangladesh.

- MV Switchgear

#### Scope of supply

General

The supply shall include all equipment and materials within the battery limits defined in this specification.

The Contractor is responsible for building the necessary main MV Switchgear for the interconnection of the Plant.  The main MV Switchgear shall be built according to the requirements of the Bangladesh Electricity Grid Code, 2018. The main MV busbar (Generation) shall have connected with Solar PV Plant, BESS and Diesel Generation. A feeder from generation bus will connect the MV busbar (distribution). There shall have 4 (four) 11 kV distribution feeder that will connect the consumer.    A feeder will be connected from the MV busbar (Generation) with the auxiliary transformer. This feeder shall be capable of servicing to street lighting, pump house, control room, office buildings, firefighting arrangements, etc. All section busbars shall be connected as shown in the figure given in Annex I  .

The Contractor shall make the work complete, down to small details and taking care of any items that may have not been specified in this Technical Specification, if the guaranteed operation parameters or the safety requirements of the plant call for these items.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Supplier.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Equipment and components

Medium Voltage switchgear shall be in accordance with codes and standards.

Any other description could be considered according to final layout proposed by the Contractor but is shall be accepted by the Employer.

Codes and standards

All the material and works must be in accordance with the most advanced practices for this type of equipment. Materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

- IEC 62271-1 High-voltage switchgear and control-gear – Part 1: Common specification

- IEC 62271-100 High–voltage switchgear and control-gear – Part 100: High voltage alternating – current circuit – breakers

- IEC 62271-102 High–voltage switchgear and control-gear – Part 102: Alternating disconnectors and earthing switches

- IEC 62271-103 High-voltage switchgear and control-gear – Part 103: Switches for rated voltages above 1kV up to and including 52kV

- IEC 62271-105 High-voltage switchgear and control-gear – Part 105: Alternating current switch0fuse combinations for rated voltages above 1kV up to and including 52 kV

- IEC 62771-106 High-voltage switchgears and control-gear – Part106: Alternating current contactors, contactor-based controllers and motor-starters

- IEC 62271-200 High–voltage switchgear and control-gear – Part 200: AC-metal- enclosed switchgear and control-gear for rated voltages above 1 kV and up to and including 52 kV

- IEC 60044-1 Instrument transformers–Part 1: Current transformers

- IEC 60044-2 Instrument transformers–Part 2: Inductive voltage transformers

- IEC 60255 Electrical relays

- IEC 60529 Degrees of protection provided by enclosures (IP Code)

- IEC 60447 Basic and safety principles for man-machine interface, marking and identification – actuating principles

- IEC 60828-1 High-voltage fuses – Part 1: Definitions, principles and rules

- IEC 61243-5 Live working - Voltage detectors - Part 5: Voltage detecting systems (VDS)

- IEC 60071-1 Insulation co-ordination - Part 1: Definitions, principles and rules

- IEC 61869-1 Instrument transformers - Part 1: General requirements

- IEC 61869-2 Instrument transformers - Part 2: Additional requirements for current transformers

- IEC 61869-3 Instrument transformers - Part 3: Additional requirements for inductive voltage transformers

- IEC 61936-1 Power installations exceeding 1 kV a.c. - Part 1: Common rules

- IEC 60376 Specification of the grade sulphur hexafluoride (SF6)

Datasheet

The technical characteristics of the MV switchgear assembly are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

The switchgear, control gear, enclosures and needed installations shall be designed taking into account the local weather conditions and the foreseen temperature at the installation location, the conditions shall not exceed the temperature-rise limits specified in the appropriate standard.

The electrical life time of the circuit breaker shall conform to IEC 62271-100 class E2, no maintenance of the circuit breaker interrupting parts for the life time of the circuit breaker and only minimal maintenance of the other parts. As a minimum the circuit breaker shall have not less than 20.000 make-break operations at full load without any maintenance or replacement of parts being necessary.

Design and construction

Housing

The individual panels of the MV Switchgear shall be of self-supporting, freestanding, metal-clad type and suitable for installation against the wall or for back-to-back installation. The panels shall only be accessible from the front. Hinged front doors shall be able to open more than 90°. The panels shall be assembled of steel members and steel sheets and equipped with bottom frames suitable for bolting to the floor construction. The bottom shall be covered with galvanized steel sheets, which are to provide with holes for cable entry.

The enclosure of each panel shall be divided into several compartments. Modules and provisions shall include some or all of the following:

- Circuit breaker / Contactor / Switch compartments and circuit breakers and or contactors and or switches

- Bus system

- Earthing / Ground bus system

- Auxiliary compartments and transformers

- Metering, protection and control devices

- Control and communication bus as required

- Connection provisions for primary, ground and control circuits

- A system allowing connection of circuit breaker and auxiliary modules with the door closed

- Assembly and module grounding utilizing a solid ground bus system throughout the equipment

- The switchboard shall be extendable on either end by removal of the end panels.

The housings have to be manufactured of sheet steel and be of welded construction. The housings have to be of a sturdy construction, conforming to the appropriate standards and be capable for service and transporting, underground and over long distances, without warping, bending or in any other way being deformed.

Compartment Partitioning/Barriers

The housing has to be constructed in such a manner that the compartments housing the busbars, circuit breaker, contactor, switch, power cable terminations, current and or voltage transformers and instruments, are partitioned from each other, by metal or similar material.

There may be other compartments embedded within others, especially for gas insulated units.

Internal Arc Classification (IAC)/Arc-Resistance

The switchgear shall be designed and constructed to ensure that personnel are protected in case of the occurrence of an internal arc.

In order to satisfy this requirement, the internal arcing tests must be done according to IEC 62271-200 and satisfy all five criteria. Test certificates proving compliance shall be produced by switchgear suppliers, to verify that testing has been carried out according to IEC 62271-200, criteria 1 to 5, for instance.

The gases generated in any of the segregated chambers (compartments) shall be safely contained or vented such that operators or personnel on floor level at the front, back or sides of the panel shall not be harmed. This would correspond to IAC Class AFLR according to IEC. The IAC shall be indicated on the Data Sheet.

Busbars

Busbars shall be single of unit length and formed from high conductivity hard drawn copper, and of uniform cross section throughout.

The busbars shall have full rounded edges. The main bus shall not be tapered. The main bus shall be in accordance with applicable industry standards for self-cooled bus ratings.

Round-bar copper plug-in busbars, insulated by means of silicone rubber, are also acceptable, especially for gas insulated assemblies.

The main and branch single busbar shall be of high conductive drawn electrolytic copper with the same cross section through all cubicles. The busbars shall have high dynamic and dielectric strength with good heat dissipation. The busbar shall be extendable at both ends; such extension shall be easily done with the minimum possible disturbance to the existing busbars. Aluminium busbars shall not be permitted.

The busbars spouts and connections from spouts to busbars are to be supported in epoxy resin or equivalent material, preferably as a 3-phase Monoblock, where applicable.

The busbar chambers are to be constructed so as to facilitate extensions in either direction with minimum shut down time.

Busbars shall be mounted at least 500mm above floor level.

Busbars unions or connections to the busbars shall be done with bolts. If bus bars sockets are used for joints, the joining method and materials are shall be fully specified and approved by the engineer.

Connection joins shall be silver plated or as per type test.

Bus bar connections shall be mechanically secured with fasteners that shall maintain adequate pressures within the operating temperature range of the switchgear.

All bus supports shall be adequate for satisfactory insulating performance and when subjected to rated normal and short-circuit currents.

Bus bars and cable colors identification shall be done according to regulations standards (IEC 60445), observing the following colors

- Phase R Black

- Phase S Brown

- Phase T Purple

- Protective Earth Green with yellow stripe

Control wires shall be black. Each wire shall be identified with withe or yellow labels and black number/letters.

Overall, phase sequence bus bars shall be R-S-T, with phase S in the middle. Phase R shall be situated (electric panel front view):

- Top for vertical line bus bar distribution

- In front for horizontal line bus bar distribution

- Left for vertical bus bar

Circuit Breaker

- The circuit breakers shall be designed to and complies with the appropriate international standard, such as IEC 62271-100 and shall be capable of meeting all the required Type tests

- The interrupting media is vacuum.

- The withdrawable parts shall be able to be inserted in the following positions:

  - "Service" position, the mobile part is completely inserted and connected

  - "Test" position, the main current circuits disconnected, auxiliary circuits connected

  - "Disconnected” position, the mobile part is completely disconnected.

- The circuit breaker shall be electrically operated with either a magnetic actuator or spring charged mechanism.

- Opening and closing speed shall be independent of the operator or of control voltage within the rated control voltage range.

- Circuit breakers of the same type, rating and control circuits shall be electrically and mechanically interchangeable.

- The circuit breaker shall include pressure loss detection in the case of SF6, arranged to trip and / or alarm and give flag indication. It shall not be possible to close the breaker under reduced SF6 pressure.

- Indication shall be provided on the front of the panel of the state of the breaker by a mechanically operated flag.

- The contact materials should have the following properties:

  - High electrical and thermal conductivity

  - Freedom from welding and high vapor pressure.

- Circuit breaker enclosures or compartment shall conform to the appropriate standards and be gas insulated. The enclosure shall be metallically segregated from the busbar compartment. It may also contain different pieces of apparatus / functional units.

- The enclosure door shall be securely held with tamper resistant hinges and a manual fastening system. Enclosure doors shall be provided with padlocking provisions.

- To ensure the personal safety of the operator it shall only be possible to operate the circuit breaker from outside of the closed cubicle front door by direct acting mechanical linkages.

- Safety shutters shall be fitted such that they automatically cover the busbar and circuit spouts when the breaker or contactor or switch is withdrawn.

- Cable mechanisms for the operation of safety shutters shall not be permitted.

- Closing Mechanism:

  - Only the following types of closing mechanisms are acceptable:

- Electrical motor charged spring, electrical release

- Electrical solenoid

  - Closing mechanisms are to incorporate anti-pumping protection

  - Control voltage: 220 Vdc (motors and spring)

  - Closing solenoid and motor charged spring shall be able to operate successfully between 190 and 250 VDC

- Tripping mechanism

  - The trip coil shall not draw more than 300 watts.

  - Substation connection circuit breaker should have two independent trip coils.

  - Provision shall be made for the additional remote tripping to be inserted in the shunt trip circuit.

  - It shall be possible to trip the circuit breaker manually from the front of the panel as follows:

- Electrically by means of a switch or push button working directly via the shunt trip and the undervoltage releases.

- Mechanically by means of a direct mechanical action on the tripping bar.

  - The emergency trip pushbutton shall latch and only be released with a key

  - Tripping system shall be able to operate successfully between 190 and 250 VDC

Interlocks

Logical Interlocks shall be provided for reasons of safety and for convenience and proper sequencing of operation, according to IEC 62271-1 Clause 5.11, with the following additions:

- Switchgear with withdrawable main switching devices

- For withdrawable units, the racking system shall allow movement of the breaker only with the closed door and have three positions, in addition to the withdrawn position (free movement):

- Disconnected: both primary and secondary contacts disengaged

- Test: primary contacts disconnected and shutters closed, but control contacts engaged)

- Connected: primary (power) and secondary (control) contacts engaged service

- It shall not be possible to insert or withdraw a closed breaker, contactor or switch

- Interference blocking shall prevent insertion of a lower rated breaker into a higher rated compartment

- All draw out modules shall have manually actuated locking devices to prevent inadvertently withdrawing a module from a compartment

- Grounding shall occur in the Test position and shall be continuous during racking and in the connected position. Grounding shall be made by solid copper contacts connecting to a solid copper ground bus.

- The interlocks shall prevent the closing of the circuit-breaker in the service position unless any auxiliary circuits associated with the automatic opening of these switching devices are connected and operational. Conversely, the disconnection of the auxiliary circuits with the circuit-breaker closed in the service position shall be prevented, and if prevention is not possible, shall cause an initiation alarm.

- Circuit breakers equipped with stored energy mechanisms shall be designed to prevent the release of the stored energy unless the mechanism has been fully charged. Operators and personnel service shall be protected from the effects of accidental discharge of the stored energy by any of the following or other suitable means:

- Interlocks provided in the housing to prevent the complete withdrawal of the circuit breaker from the housing when the stored energy mechanism is fully charged.

- A suitable device to prevent the complete withdrawal of the circuit breaker until the closing mechanism is blocked.

- A mechanism provided to automatically discharge the stored energy before or during the process of withdrawing the circuit breaker from the housing. If the stored energy is discharged before the circuit breaker is moved from the connected position, an adjunct electrical interlock is required to prevent stored energy re-charge.

Earthing Switch

- The earthing facilities should be integral in the switchgear design to allow earthing of the outgoing cable side only of the circuit breaker, contactor or switch.

- The earthing should preferably be carried out through the circuit breaker in which case the electrical tripping shall be isolated and the mechanical trip bar locked in the healthy conditions.

- Visual indication is to be provided on the front of the panel to indicate that the circuit breaker is in either the "Normal Service" or "Circuit Earth" position. The switchgear is to be provided with full padlocking facilities in both the "Normal Service" an "Circuit Earth" positions

- Earthing switch shall be combined with the disconnector (load break switch) as a single unit, the rated short-time withstand current of the earthing switch shall, unless otherwise specified, be at least equal to that assigned to the disconnector.

Earth Bar

- The earth bar shall be uninsulated and is to be made from hard drawn, high conductivity copper of minimum cross section dimension of 200 mm2.

Current Transformers

- The current transformers shall preferably be installed in a separate chamber from the main switching devices. Transformers should be installed in an easy inspection and replacement place.

- They shall be epoxy resin insulated and of the bar or wound primary type according to the ratio, class and accuracy.

- Current transformers shall be designed for continuous thermal current rating equal to the current rating of the associated feeder (or the expected operating current) plus 20% over-load as well as for a short time current rating corresponding to the relevant fault level of the switchgear. Accurate measuring is also required during low production phases.

- The current transformers shall preferably have a secondary current of 5 Amps. The Current Ratios shall be stated on the data sheet.

- Accuracy, type and class of current transformers for the Plant Main Circuit Breaker and the energy metering shall comply with the Bangladeshi Transmission Grid Code.

Voltage Transformer

- The voltage transformer shall be a 3-phase, 3-limb, withdrawable pattern unless otherwise specified. The windings are to be encapsulated in epoxy resin.

- Transformers should be installed in an easy inspection and replacement place.

- Safety shutters, which can be padlocked in the closed position shall be arranged to seal off the spouts when the voltage transformer tank is withdrawn.

- The voltage transformer may be busbar connected or cable connected.

- The voltage transformer shall be fitted with a set LV fuses or circuit breaker and should be readily accessible. MV fuses shall be optional.

- Normally all three windings of the voltage transformer shall be equally rated.

- Accuracy, type and class of voltage transformers for the Plant Main Circuit Breaker and the energy metering shall comply with the Bangladeshi Transmission Grid Code.

Instrument Chamber

An instrument panel for the mounting of relay instruments, meters and control fuses shall be provided. The relay panel shall be protected against the ingress of contaminants to IP54 as defined by IEC 60529.

Door to be adequately reinforced to support relays etc.

All instruments and relays to be mounted on door and be visible without opening of door.

Meters and Instruments

All instruments and meters shall be protected by nonreflecting glass. Each incoming and outcoming cubicle feeder shall have one multimeter with the following characteristics:

- The instrument should be able to withstand momentary overloads of 20 times rated current.

- Auxiliary supply shall be 220V DC.

- Digital meters shall be used either to display single variables or as combined meters to display various variables / quantities. The meters may have memory to store specified values e.g. Maximum reached values or events

- The display window dimensions, size of digits and number of digits shall be approved by the Engineer

- Unit display could be able to combining all the protection, control, measurement etc.

- This may also make it possible to dialogue with the installation control and automation systems, allowing plant data acquisition and processing

- Indicators

- Multimeter should meter at least the following measures:

- Voltage measurement (Ph/Ph and Ph/N)

- Current measurement for each phase (bidirectional)

- Kilo-Watt measurement (bidirectional)

- Kilo-Var measurement (bidirectional)

- PF measurement

- Frequency measurement

- Kilo-Watt-hour measurement (bidirectional)

- Kilo-Var-hour measurement (bidirectional)

- A power quality meter for measurement of current and voltage harmonics shall be installed at the grid connection point.

Protection and Control

Each incoming and outcoming cubicle feeder shall have one individual digital protection relay, with the following characteristics:

- All protection relays shall be plug-in type with contacts rated at 10A, and facilities for secondary injection testing and indication of the trip or alarm condition

- Control relays shall be of an industrial pattern plug-in type. The relay base must have screw type terminals

- It shall be possible to set or reset relays from a standing position in front of the switchgear panel, particularly where the relays are mounted in a relay chamber

- In the case of on-board protection, protection equipment shall be mounted on or inside the relay chamber

- Control rated voltage shall be 220 VDC

- Control relays should have at least the following protections:

  - Busbar

  - Minimum voltage (ANSI 27)

  - Zero sequence overvoltage shall be provided to detected internal ground faults of the 33-kV system with delta vector group transformer (59 N)

  - Circuit breakers

  - Overcurrent time (ANSI 51)

  - Overcurrent inst. (ANSI 50)

  - Ground fault (51N)

The requirements for protection devices and functions have to be complied with the Bangladesh Electricity Grid Code, 2018.

Panel Wiring

A minimum size of 2.5 mm² stranded copper conductor shall be used for all panel wiring. Only control wires could have 1.5 mm² section.

It is preferred that the control wiring be run in horizontal and vertical PVC ducts.

All conductors shall be identified and marked.

Grommets are to be installed where conductors pass through the metal work.

Anti-Condensation Heaters

Anti-condensation heaters shall be installed in each cubicle, with thermal and humidity control device.

Heater should be feed with external 220 VAC source

Labels

The front panel shall have a single line mimic, indicating the busbar, main switching devices and earthing switch, voltage transformers and or capacitive voltage indicators, mechanical (and where specified electrical) main switching devices and earth switch positions.

Labels shall be provided for all relays, timers, pushbuttons, indicating lamps and other equipment mounted on the face of the panel and internally.

A label shall be provided adjacent to each fuse indicating the circuit and fuse rating.

Each panel shall be labeled at the front and rear, showing the panel number and designation. These labels are to be permanently fixed to a non-removable portion of the panel.

There shall be affixed on the switchgear assembly, labelling indicating the nominal Medium voltage and the name of the switchboard, corresponding to the single line diagram.

Current transformer detail label to be installed in the instrument chamber.

Cable Termination

- Cable compartment

    - The clearance in the cable termination box shall be suitable for air clearances.

    - The dimensions of the cable termination box shall be chosen considering the number of cables to be terminated, the termination method and make of termination hardware (i.e. T plug, cable plug, coupling plug, elbow plug or adapter etc.) requirement for installation of and dimensions of surge arresters, space for any other hardware in the cable compartment.

    - Since the size of the cable compartment shall be chosen from the manufacturer’s type tested designs, details of any hardware not supplied by the switchgear manufacturer that is required to go into the cable compartment shall be communicated to the manufacturer.

- MV termination

    - Termination shall preferably be accomplished with bolted cable connections, with cable elbow plugs or T-plugs and cable sealing ends for bushings according to EN 50181 or similar with outside cone and bolted contact.

    - Facilities for cable testing, without removal of the cables shall be incorporated in the termination arrangement e.g. removable protective cap and / or end stopper from cable plug.

- LV termination

    - A LV cable termination box is to be provided separate from the MV cable box and shall have a removable gland plate.

    - A terminal strip having adequate room for cables above the gland plate shall be provided.

    - It shall be possible to bus wire between panels from one cable termination box to another using conventional wiring, twisted pair, Ethernet or fiber optic cable.

#### Tests

A comprehensive FAT (tests according to IEC 62271) has to be conducted and witnessed by the Employer, the Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests, a test procedure shall be submitted to the Employer for the approval.

#### Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall be in compliance with the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts (spare parts are quoted as optional).

The warranty period must be two (2) years and it shall begin from the provisional plant acceptance.

This warranty implies that the Supplier shall repair, or replace if necessary, all the elements damaged during this period.

#### Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Technical data sheets

- Layout drawings of the switchgear including all cubicles

- Electrical schematics and Wiring Diagrams incl. termination drawings

- Warranty

- Protection relay schedule

- Spare parts list

- Operation and maintenance manual including component list with manufacturer in-formation e.g. catalogue, etc.

- Reports of tests and commissioning with protocols Tests.

- LV Switchgear

#### Scope of supply

General

The supply shall include all equipment and materials within the battery limits defined in this specification.

The Contractor shall make the work complete, down to small details and taking care of any items that may have not been specified in this Technical Specification, if the guaranteed operation parameters or the safety requirements of the plant call for these items.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Supplier.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Equipment and components.

LV Panels necessary according to single-line Diagram located inside precast buildings.

Any other description could be considered according to final lay-out proposed by the Contractor but is shall be accepted by the Employer.

#### Codes and standards

All the material and works must be in accordance with the most advanced practices for this type of equipment. All the materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The LV power distribution panels shall comply with this Specification and latest revision of the following IEC Publications:

- IEC 60038 	Standard voltages.

- IEC 60059 	Standard current ratings.

- IEC 60158 	Low-voltage control-gear for industrial use.

- IEC 61439-1 	Low voltage switchgear and control-gear assemblies - Part 1: General rules.

- IEC 61439-2 	Low voltage switchgear and control-gear assemblies - Part 2: Power switchgear and control-gear assemblies.

- IEC 60408 	LV Air-break Switches, Air-break Disconnectors, etc.

- IEC 60185 	Current Transformers.

- IEC 60186 	Voltage Transformers.

- IEC 60269 	LV Fuses.

- IEC 60947-1 	Low Voltage Switchgear and Control gear – Part 1: General rules.

- IEC 60947-2 	Low Voltage Switchgear and Control gear – Part 2: Circuit Breakers.

- IEC 60947-3 	Low Voltage Switchgear and Control gear – Part 3: Switches, disconnectors, switch-disconnectors and fuse-combination units.

- IEC 60947-4-1 	Low Voltage Switchgear and Control gear – Part 4-1: Contactors and motor-starters – Electromechanical contactors and motor-starters.

- IEC 60044-1 	Instrument transformers – Part 1 : Current transformers.

- IEC 60044-2 	Instrument transformers – Part 2 : Inductive voltage transformers.

The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

#### Design and construction

General

All electric panels shall be fully assembled in the factory, including all internal cabling. Thus, during commissioning only external connections shall be necessary.

All accessories shall be supplied for the unions between electric panels and bus bars, indicating the corresponding tightening torque.

All support structures for electrical equipment shall be designed to suit the service conditions specified, the loads imposed on them, and any appropriate electrical clearance requirements

Metal fabrication.

Electric panels shall be built of cold laminated profiles of steel, folded and/or welded/screwed of a minimal thickness of 2.5 mm. Metal enclosure should have at least a thickness of 2 mm.

Panels shall be self-holding and rodent proof. Electric panels shall be prepared to be anchored to the floor with bolts or similar (supplier shall indicate the anchored system).

All screws, bolts, and fixing elements shall be of steel treated against corrosion. These elements shall not be painted.

Panels shall be provided with top hoisting eyes for the transport and elevation. These shall be detachable and the corresponding drills shall remain totally closed with stoppers, when hoisting eyes are extracted.

All non-metallic elements (terminals block, cable channels, clamps, etc.) shall be of hygroscopic material and no flame spread. Cables shall not be spliced, and two wires or more shall not be connected to the same terminal.

Earth connection shall be the last one disconnected and the first one connected.

The opening doors shall have neoprene joints.

All doors shall be designed to be used and managed in an easy and sure way, without special tools. Nevertheless, special tools shall be needed to open bus bars compartments.

Electric equipment and connections

All power and control circuits with voltage could be managed safely from the exterior of the electric panel, doing the following.

- Electric command (open/close).

- Inspection in service of electric protections, control, alarms or safety measures.

- Position limit contacts of breakers shall withdraw vibrations.

Bus bars

Main bus bars shall be made of electrolytic cooper with high conductivity. Bus bars shall be dimensioned for constant operation at nominal current. Electric contact parts should be silvered.

Bus bars supports and dividers shall be insulated and non-flame spread properties. These supports shall allow only longitudinal expansion.

Inside bus bar compartment, shall not be possible to install any type of auxiliary wire.

All connections between different bus bars shall be done with cupper strings. These connections couldn´t be done with flexible wire. Unions of main bars shall be done with cadmium steel screws of high resistance, nut, washers and other mechanisms to avoid loosening.

Bus bars shall be separated according to rated voltage. Moreover, bus bars shall have an insulated ribbon or cover.

Main bars, unions, screws, supports, etc. shall be measured to support the dynamic effects of current peaks during short circuits.

Low voltage bus bars and cable colors identification shall be done according to standards (IEC 60445), observing the following colors

- Phase R Black

- Phase S Brown

- Phase T Purple

- Protective Earth Green with yellow stripe

Control wires shall be black. Each wire shall be identified with white or yellow labels and black number/letters.

Overall, phase sequence bus bars shall be R-S-T, with phase S in the middle. Phase R shall be situated (electric panel front view):

- Top for vertical line bus bar distribution

- In front for horizontal line bus bar distribution

- Left for vertical bus bar

Earth bus bars: There shall be independent earth bus bars for each vertical section. All internal equipment with a metallic frame and protection wire shall be connected to an earth protection, with an uninterrupted connection.

Control.

Control devices shall be installed on front panels. As far as possible, control rated voltage shall be 220 VDC.

Primary and secondary terminals shall be indelibly marked.

Measurements and power transformers shall be dimensioned (power and accuracy class) to guarantee accuracy during overloads and short-circuits. Furthermore, transformers shall stand good for selective protection.

Measurement devices

Measurement devices shall be according to IEC 51-255-348 and 688 recommendations.

Equipment for measuring shall be installed in a visible and accessible spot.

Cable and terminals.

The lower part of the cubicle shall house the terminal strips and connecting blocks. Terminals shall be fitted in an easily accessible position, with enough space for inspection and maintenance.

If parallel connection of more than 2 cables in parallel is required, copper straps shall be used to carry it out.

Supports and clamps for vertical wires shall be provided. These clamps shall be adapted to allow the earth connections of metallic covers of the cables. Special precaution shall be taken to guarantee that there isn´t any magnetic circuit closed around the single-pole cables, or any cable that could be submitted to an unbalanced load.

Terminal blocks for power and control circuits shall be insulated with polyamide, and installed on standardized rails. Conductor tightening shall have a losing and shearing protection system.

Incoming and outgoing terminal boxes shall be installed height enough to allow external cable connection without overcoming its radio of curvature

In offer phase, manufacturer shall certify quality and homologation of their terminal blocks.

Current circuits shall be provided with short-circuit terminals.

Wire up shall be done according to the electric diagrams. All internal wiring shall be done by the electric panel manufacturer. Remaining wire up shall not be admitted. Only those cases of last-minute modifications, manufacturers and Employer shall determine place and form to finish pending wiring.

Terminals and connectors shall be right dimensioned and identified, according to the electrical diagrams. Manufacturer shall take special attention to distance between terminals. 10% of overall number of terminals should be left as equipped reserve. A minimum of one spare terminal rated size.

Identification labels.

Identification labels shall be made of non-corrosive white rigid plastic. Letters shall be etched in black color. Inscriptions shall be clearly legible from the normal operation distance.

Each LV Panels shall be identified with a laminated plastic with black letters, placed on the top electric panel. Sign shall be fixed with two screws.

Height of the text for the principal and secondary labels shall be confirmed later.

All internal equipment shall be identified with laminated plastic. Identification text shall be according to developed electric schemes.

Equipment placed on front panel shall be identified with plastic labels, laminated, rigid and black color. White identification text shall be according to developed electric schemes.

#### Tests

A comprehensive SAT and FAT has to be conducted and witnessed by the Employer, the Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests, a test procedure shall be submitted to the Employer for the approval.

#### Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall be following the specifications hereto and shall be unused products, free from any defects in design, material or workmanship.

The warranty period must be two (2) years and it shall begin from the provisional plant acceptance.

This warranty implies that the Supplier shall repair, or replace if necessary, all the elements damaged during this period.

#### Data Sheet

The technical characteristics of the LV switchgear assembly are detailed in the data sheet (placed at the Volume 3 of 3 of this document).

The distribution boards shall consist of factory built, standardized panels and/or units for incoming feeders, bus ties, motor feeders, etc.

The LV distribution boards shall be of robust construction, type-tested, self-supporting, multi-cubicle type assemblies designed according the requirements of IEC 61439.

Distribution boards shall be designed to give the maximum reliability during service, giving regard to the need of speed and ease of inspection, testing and maintenance.

All electric panel boards shall withstand without damage or permanent deformations in the mechanical and thermal requests produced by nominal intensity or short circuits.

A metallic removable cover for all the incoming/outcoming cables shall be arranged.

All internal equipment with a metallic frame shall be connected to the earth protection, with an uninterrupted connection. Each side of the copper strip (earth protection) shall have a terminal jaw with two screws.

All necessary mechanical interlocks shall be provided to prevent faulty operations.

The following equipment shall be fully enclosed in separated sheet metal compartments to provide electrical segregation:

- each circuit breaker

- each section of main bus

- each set of potential transformers

- each set of low voltage devices such as relays, instruments

- control wiring and termination blocks

- each power cable termination compartment

All LV incoming feeders shall be provided with power monitoring units with local indication of voltage, current, energy and power consumption. This information shall be sent to the PCMS with bus connection.

A single voltmeter with changeover switch must be provided for measurement of bus bar voltage between each phase. Measuring instruments should, in general, be square in shape.

LV Panels shall be equipped with an automatic fast-transfer switching logic which controls incoming circuit breakers and bus coupler (where applicable) in order to keep both bus bars in service without long interruption time. When breakers shall be switched back to normal condition, bus bars shall be kept in service without interruption

### 2.11.8 LV/MV CABLE AND ACCESSORIES

Low Voltage (LV) and Medium Voltage (MV) cable and accessories shall be designed to be highly efficient and provide a reliable system operation in accordance with the internationally proven standard system and existing climatic conditions of Bangladesh.

### 2.11.8.1 MV Cable and Accessories

All MV cabling shall be underground mounted, using water-resistant cable.

#### Scope of supply

General

The supply shall include all equipment and materials within the battery limits defined in this specification.

The Contractor shall make the work complete, down to small details and taking care of any items that may have not been specified in this Technical Specification, if the guaranteed operation parameters or the safety requirements of the plant call for these items.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Supplier.

Should any contradiction arises among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Equipment and components

The equipment to be supplied by the Contractor are the following:

- Medium Voltage cables.

#### Design Criteria for AC Cables

The aggregated voltage drop for AC cables will be 1% at the plant’s nominal output under any weather condition. Voltage drop calculation shall be submitted to the Employer’s Engineer for approval prior to purchasing and installation.

#### Codes and Standards

All the material and works must be in accordance with the most advance practice for this type of equipment. All the materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

- IEC 60228 Conductor of insulated cables

- IEC 60229 Test on cable over sheath which have a special protective function and are applied by extrusion

- IEC 60230 Impulse tests on cable and their accessories

- IEC 60811 Common test methods for insulating and sheeting materials of electric cables

- IEC 61238 Compression and mechanical connectors for power cables copper or Aluminium conductors

- IEC 60502 Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1,2 kV) up to 30 kV (Um = 33 kV)

- IEC 60986 Short-circuit temperature limits of electric cables with rated voltages from 6 kV (Um 7,2 kV) up to 30 kV (Um =33 kV)

- IEC 60840 Power cables with extruded insulation and their accessories for rated voltages above 30 kV (Um = 33 kV) up to 150 kV (Um = 170 kV) - Test methods and requirements.

The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

#### Constructive characteristics

General

Medium voltage cable shall be single-core or three-core copper or Aluminium cable. Cable shall be composed of the following elements:

- Conductor

- Insulation

- Screen

- Sheath

Cable shall be no flame spread (IEC 60332). Low smoke emissions properties shall be appreciated.

Conductor

The conductors shall consist of several stranded wires of copper (class 2 according to IEC 60288), physical, mechanical and electrical characteristics, according to the regulations. Also wires of Aluminium shall be considered as option.

Insulation

The conductor insulation is resistant to damp, heating, and aging, also it has a good resistance to ozone.

Insulation shall be extruded dielectric of cross-linked polyethylene (XLPE).

The insulation thicknesses are according the normative.

Cable insulation shall be made up of three extruded layers:

- Conductor semi-conductive layer

- Insulation (XLPE)

- Insulation Semi-conductive layer

The thickness of any separator or semi-conducting screen on the conductor or over the insulation shall not be included in the thickness of the insulation.

Metallic Screening/Shielding

The metallic screening (bare copper wires) over insulation semi-conductive layer is necessary to cancel out the electric field outside the cable and to provide a low resistance path for charging current to flow to ground.

Three-core cables shall be designed with individually screened cores.

Armor

Exterior cables buried direct in the ground shall have armor, to provide mechanical protection to the cable.

Armor shall consist of round or flat wires of galvanized steel. Only for single-core cables shall consist of non-magnetic material, such as Aluminium.

Sheath

The outer sheath shall be composed by PVC or similar. It has good resistance to moisture and it is suitable for the installation in a trench buried or on a tray or stapled to the wall.

The cable shall have its outer sheath marked with its cross section and length in a progressive way.

#### Tests

A comprehensive FAT has to be conducted and witnessed by the Employer, the Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests, a test procedure shall be submitted to the Employer for the approval.

#### Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall be in compliance with the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts (spare parts are quoted as optional).

The warranty period must be two (2) years and it shall begin from the provisional plant acceptance, provisional take over.

This warranty implies that the Supplier shall repair, or replace if necessary, all the elements damaged during this period.

#### Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Cable lists

- Technical datasheets for each cable type

- Block diagrams

- Cables sizing and voltage drop calculations.

### 2.11.8.2 LV Cable and Accessories

#### Scope of supply

General.

The supply shall include all equipment and materials within the battery limits defined in this specification.

The Contractor shall make the work complete, down to small details and taking care of any items that may have not been specified in this Technical Specification, if the guaranteed operation parameters or the safety requirements of the plant call for these items.

The equipment to be supplied shall also be designed so that all provisions for easy access for inspection, cleaning, maintenance and repair are accounted for. The inspection facilities and openings required for this are to be included as well.

The Contractor shall take care that all components necessary for a safe and trouble-free operation are included in the scope of supply. Also, individual parts which are not explicitly mentioned but which are necessary for proper operation shall be included in the scope of supply without additional cost to the Employer.

The scope of supply comprises complete and operational new equipment corresponding to the state of the art, which is to be integrated into the overall plant concept. The scope of supply shall include all components required to ensure safe and proper operation as well as maintenance of the main and associated equipment under the scope of this supply.

The Contractor shall supply equipment of a well-proven design in similar applications (prototypes shall not be permitted). The supply shall be in accordance with the terms and conditions of this specification as regards to the requested performance, design criteria, construction requirements, guarantees and time schedule.

The equipment supplied by the Contractor shall be in accordance with the terms and conditions of this specification. Nevertheless, it is not the intention of this document to provide full description of the equipment to be provided. All requirements or recommendations commonly established for the design, material selection, fabrication, inspection, testing, preparation for shipment and commissioning of this type of equipment and installations shall be complied according to good practice and are in the scope of the Supplier.

Should any contradiction arise among the various requirements included in this technical specification (and annexes), the other contractual technical specification and/or the applicable standards or regulations, the one to be applied is the most restrictive one, which gives better performance or benefit to the Employer. In any case, the Employer reserves the right to fix which of the different requirements are to be complied with. In the case that such a contradiction arose, only the Employer by a written statement is able to decide which the compulsory requirement to be finally applied is.

The Contractor shall provide, if necessary, adequate technical and maintenance assistance to the Employer related to its scope of supply.

Equipment and components.

The equipment to be supplied by the Contractor are the following:

- Low Voltage power cables.

- Low Voltage control cables.

#### Design Criteria for DC Cables

The aggregated voltage drop for DC cables will be 1.5% at the plant’s nominal output under any weather condition. Voltage drop calculation shall be submitted to the Employer’s Engineer for approval prior to purchasing and installation.

#### Codes and standards

All the material and works must be in accordance with the most advance practice for this type of equipment. All the materials and realized works shall be in accordance with latest edition of the IEC recommendations.

The delivery and the equipment in it shall be designed to meet the requirements of the following codes and standards:

- IEC 60228 Conductor of insulated cables

- IEC 60614 Specification for conduits for Electrical Installations

- IEC 61238 Compression and mechanical connectors for power cables copper or Aluminium conductors

- IEC 60304-1 Standard colors for insulation of low frequency cables and wires

- IEC 60502-1 Cables for rated voltages of 1 kV ((Um = 1,2 kV) and 3 kV (Um = 3,6 kV)

The design, materials, manufacturing, transportation, inspection, tests and packaging of the equipment and systems supplied shall be carried out as per International practices.

#### Technical Characteristics

The technical characteristics presented by the low voltage cable are:

| Low Voltage | Units |  |
| --- | --- | --- |
| Working voltage | V | 400/220 AC – 220 DC |
| Rated voltage | kV | 0.6/1 |
| Maximum rated Voltage | kV | 1.2 |
| Conductor |  | Copper |
| Insulating material |  | XLPE |
| Armored |  | Yes |
| Sheath |  | PVC or similar |

#### Constructive characteristics

General

Power and control cables shall be manufactured in accordance with the international standards. They shall have stranded copper conductors, insulation, 0.6/1 kV voltage grade, separation tapes and sheath.

Control cables should have common core screen and protection against induction influence.

The minimum conductor cross section of the low voltage power cables is 2.5mm2.

Cable shall be no flame spread (IEC 60332). Low smoke emissions properties shall be appreciated.

Conductor

The conductor shall be uncoated annealed copper and shall be compacted and stranded.

Copper power cable shall be soft drowning multi-strands with a minimum number of strands as is specified in the relevant IEC.

Insulation

The conductor insulation shall be resistant to moisture, heating and aging of cables to be used in systems with greater phase voltage of 1,000V. Also, the cable shall have good resistance to ozone and sunlight.

The insulation shall consist of XPLE, EPR or similar.

The nominal insulation thickness shall be as per values specified in IEC 60502-1, with respect to voltage rating and cable cross-section.

Screen

The metallic screening (bare copper wires) over insulation semi-conductive layer is necessary to cancel out the electric field outside the cable and to provide a low resistance path for charging current to flow to ground.

Only specific application with control cables shall have screen.

Armor

Exterior cables buried direct in the ground shall have armor, to provide mechanical protection to the cable.

Armor shall consist of round or flat wires of galvanized steel. Only for single-core cables shall consist of non-magnetic material, such as Aluminium.

Sheath.

The outer sheath material shall be black PVC, ST2 type (90ºC max. conductor temperature) as per IEC 60502-1.

The nominal thickness of the outer sheath shall be as per IEC 60502-1.

Marking

The jacket for all cables shall be marked by embossing at intervals not exceeding one meter with the following minimum information:

- The manufacturer's name

- Voltage designation

- Type of insulation, XLPE

- Conductor size and material

- Year of manufacture

- Cumulative length at every meter with the highest length mark on the outer end of the cable.

#### Tests

A comprehensive SAT and FAT has to be conducted and witnessed by the Employer, the Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests, a test procedure shall be submitted to the Employer for the approval.

#### Guarantees

The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

The Supplier shall guarantee that the supplied equipment, material, or part thereof shall follow the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts (spare parts are quoted as optional).

The warranty period must be two (2) years and it shall begin from the provisional plant acceptance, provisional take over.

This warranty implies that the Supplier shall repair, or replace if necessary, all the elements damaged during this period.

#### Documentation

The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Cable lists

- Technical datasheets for each cable type

- Block diagrams

- Cables sizing and voltage drop calculations

### 2.11.9 Plant Control and Monitoring System

This chapter specifies the minimum requirements for the design, delivery, installation and testing of the overall Plant Control and Monitoring System (PCMS). The system shall be modern, state of the art and provide similar functionality and easy handling like renowned standard market solutions from Meteocontol, Gantner Instruments or equivalent.

The Contractor shall comply with all the requirements of the Employer to operate.

- Specification

The PCMS shall communicate efficient over different interfaces and networks with all devices to be monitored in the Plant:

- Inverters

- String monitoring

- Transformer sensors

- Switchgear

- BESS

- 11 kV distribution system

- Energy Meter

- Grid Power Analyzer (Local 11kV Grid)

- Meteorological measurement stations

- Workstation in the Control Building

- Archive data storage

The PCMS shall provide the following functions:

- Monitoring of the inverter and the string performance

- Analysis of the Solar PV Plant performance (Performance Ratio).

- Analysis of BESS performance

- Analysis and evaluation of actual energy production and status of the PV Plant.

- Analysis and evaluation of energy stored in and supplied from BESS

- Monitoring of Diesel Generator Set

- Monitoring of SVG

- Logging and archiving of all events, meteorological data, yield, alarms, system & hardware failure, including analysis and self-monitoring, etc.

- Reporting and announcement management for alarms, warnings. events, diagnostic (hardware and software).

- Acquisition, printout and display of reports, events, individual equipment alarms with date and time stamp, including data export function to office programs as per Excel, Word; PDF; etc.

- Authorization levels and definition of user rights (log in/off).

- Remote control and monitoring / fault detection.

- Modular hardware and software.

- Ease of operation.

- Equipment shall be suitable for continuous operation.

- The data of PCMS shall be available at the Web Portal.

The PCMS shall require the following parameters:

- Inverter

1. DC Voltage (V)

2. DC Current (A)

3. DC Power (kW)

4. AC Voltage Phase 1 (V)

5. AC Voltage Phase 2 (V)

6. AC Voltage Phase 3 (V)

7. AC Current Phase 1 (A)

8. AC Current Phase 2 (A)

9. AC Current Phase 3 (A)

10. AC Voltage rms (V)

11. AC Current rms (A)

12. AC active Power (kW)

13. Reactive power (kVAr)

14. Apparent Power (kVA)

15. Power factor (cosphi)

16. Efficiency (%)

17. AC Total Energy (kWh)

18. Alarms codes (as per inverter manufacturer).

19. Inverter Status (as per inverter manufacturer).

- Data Connection (communication status for that inverter)

- BESS

- State of Charge

- Current

- Voltage

- Temperature

- AC active Power (kW)

- Reactive power (kVAr)

- Apparent Power (kVA)

- Power factor (cosphi)

- Efficiency (%)

- AC Total Energy (kWh)

- Alarms codes (as per BESS manufacturer).

- Inverter Status (as per BESS manufacturer).

- MV Switchgear / Substations

1. Modular DI/DO modules.

2. Modular AI modules for Pt100/Pt1000, 4-20mA, 0-10V inputs, with at least 4 of each.

- Parameters advisable from generating transformer:

1. Oil level (alarm + trip)

2. Oil temperature (alarm + trip)

3. Pressure relief (alarm + trip)

- Parameters advisable from the Energy Meter:

1. Voltage Phase 1 (V)

2. Voltage Phase 2 (V)

3. Voltage Phase 3 (V)

4. Current Phase 1 (A)

5. Current Phase 2 (A)

6. Current Phase 3 (A)

7. Active Power (kW)

8. Reactive power (kVAr)

9. Apparent Power (kVA)

10. Power factor (cosphi)

11. Frequency (Hz)

12. Total Exported Active Energy (kWh)

13. Total Imported Active Energy (kWh)

14. Total Reactive Energy (kVArh)

18. Data Connection (communication status for that meter)

- Hardware and Software Requirements

#### General Requirements

The Contractor shall provide standard hardware and software configurations to the extent possible as long as it meets or exceeds the requirements of this specification. International standards shall be applied for hardware and software interfaces to allow system expansion in terms of equipment and software functions if required.

#### System Security

The PCMS or each subsystem shall be designed in accordance to ISO 27002, ISA 99 or equivalent Standard.

For security reasons all log-in and log-out events shall be logged in the event list. All user changes and modifications to the system as well as parameter and program modifications shall be logged with the exact time and operator’s assignment in the event list too. It shall be possible to print this information.

#### Performance and Reliability

- All equipment shall be of high quality and reliability. The overall system availability of the PCMS shall be 99% or higher.

- Loss of monitoring data shall be avoided by means of redundant hard disk drives or RAIDs and an appropriate automatically operating backup technology for removable media.

- All equipment shall be protected against cyber-attacks and shall be certified by CE signs for operational safety.

- The PCMS-System shall have a minimum lifetime of 25 years.

#### Software Requirements

The PCMS shall be based on standard proven firmware and software. There shall be references of successful installation and operation of the used software and hardware available. The software engineering tool shall be provided to configure, set up and modify the data acquisition, data processing and database system components. The software application shall include facilities to perform programmable logic functions.

The system shall have monitoring and self-diagnostics features for both, hardware and software.

The system shall provide a solution that needs to be flexible for Employer’s requirements in terms of asset management and O&M supervision.

The system shall allow for individual reporting or consolidated reports by portfolio. Portfolio can be considered as a cluster of plants defined by the Employer.

The system shall display all the required parameters per asset management individually of clustered in portfolio. The parameters indicated shall include, but not be limited to: performance ratio, system availability, insolation and exported energy.

A licensed software copy required for the proposed system shall be provided. The latest proven antivirus software shall be installed in the P

CMS.

All logins to the system shall be password protected. Data transmission via public inter-net shall be encrypted.

#### Spare Parts and Upgrades

The Contractor shall guarantee that spare parts shall be available during the entire Design Life.

The Contractor shall ensure the availability of firmware and software upgrades are free of charge for the lifetime of the system.

#### Redundancy Concept

- Any single component can cause a complete outage; it shall be designed as redundant equipment and for higher reliability, ease of access to any component of the plant, ease of maintenance and replacement, and quick system backup support;

- If a failure in an instrument or in a control component can directly or indirectly cause the failure of the whole system, this component shall have a redundancy factor 2.

- The trip or outage of any single equipment or any single piece of auxiliary equipment shall not affect the operation of the remaining, i.e. priority shall be given to stability of the electrical grid system. The impact of the failure on plant power output shall be minimal and shall not lead to the loss of the total plant power output.

#### Over-Voltage Protection

Those parts of the system that are electrically connected to cables leaving a building shall be fitted with cascaded over-voltage protection.

#### Grounding

The PCMS equipment shall be connected via a common potential equalization bar to the earthing network of the system.

#### Ambient conditions

- Ambient conditions for Outdoor Equipment shall withstand a minimum temperature range between 0°C and 65°C and a Relative Humidity between 0% and 95%.

- Ambient conditions for Indoor Equipment in LV cabins shall withstand a minimum Temperature range between 0°C and 55°C and a Relative Humidity between 0% and 95%.

#### Labelling and Marking

All terminals, plugs, internal and external connecting cables shall be labelled durable and readable in English with a code approved by the Employer/Employer´s Engineer.

#### Power Supply

Redundant power supply including Uninterruptible Power Supply (UPS) for PCMS shall be provided. All central units, workstations and data archiving servers shall have redundant power supply. Also, the data loggers and the Ethernet Network shall be equipped with UPS systems. The capacity of the UPS shall provide enough energy for at least three (3) hours of operation of the PCMS.

#### UPS

As a standby source, the control room shall have adequately sized UPS system with a minimum back up of three (3) hours. The UPS system shall essentially include deep discharge Valve-Regulated Lead Acid (VRLA) battery bank and mounting racks as required for completing the installation.

#### Cabling

All cables and cable laying works including accessories for the PCMS are in Contractor’s scope

For Ethernet connectivity interfaces, only shielded cables of type CAT 6a / Single Twisted Pair (STP) or better shall be applied in a structured cabling according to ISO 11801.

In case of use of Fiber Optic Cables (FOC), single mode type, metallic free and certificated for outside / buried laying at local ambience conditions shall be used. Spare fibers of 6 pair for update or future extension shall be foreseen. All fibers shall be terminated in patch panels ready for use.

#### Workstation

The performance, memory and hard disk of the operator workstation shall be sufficient to comply with the requirements specified in this document.

The workstation shall be installed inside the Control Room within the Electrical and Control Buildings.

The operator workstation shall have as minimum the following specification:

- PC, CPU: e.g. Intel Core i5, 3 GHz 64Bit

- 8 GB RAM

- Graphic Controller, at least dual ports, resolution HD1080, DVI/HDMI outputs

- RAID 5 – System (Hard disk for archiving system)

- High quality keyboard and optical mouse

- 2 x 100/1000 Base T LAN interface

- UPS Power supply.

The workstation shall have redundant LCD monitors with the following specification as a minimum:

- 32 Inch LCD TFT

- High Resolution

#### Human Machine Interfaces

The Workstation shall be supplied with an operator GUI including LCD monitors, keyboard and mouse to perform all operational and engineering functions from the Control Room. The Workstation shall have minimum but not limited to the following interlinked display graphics:

- Plant Overview

- Single Line Diagrams (overview and detail for different voltage levels)

- Alarm and event management incl. Alarm list (s) and Event list (s)

- PCMS architecture along with communication network

- Diagnostic screen including overall system architecture

- Graphical windows shall be freely arranged on screens, etc.

The layout, color coding and the final number of the graphic displays implemented by the Contractor shall be decided during design/commissioning phase and with the approval of the Employer/Employer’s Engineer.

Each display shall show the current value and status of all measured data. Value in alarms shall appear flashing in real time. The status indication of picture elements such as breaker ON/OFF shall be shown by color coding. Each analogue value shall be shown with its proper accuracy and engineering units.

#### Printer and Accessories

A laser printer shall be provided.

#### Archiving Server System

For regular backup of the RAID data storage array a Network Attached Storage unit (NAS) shall be provided.

The unit shall have a sufficient capacity to allow:

- Complete backup of the server and workstation operating system files and application programs – this backup to be done by the system administrator on monthly basis.

- Daily backup of the Plant Surveillance System user and event database and other system files that change during daily operation. For video backup only selected events shall be considered. The unit shall be capable to ensure backup capacity of those files for a continuous period of 6 months.

An alarm shall be raised when the NAS capacity decreases to less than 20%.

Equipment for automatic backup of workstation shall be provided. Removable media (e.g. hard disk, DVD or similar) shall be provided to enable storage of backups.

#### Data Logger

Technical data of data logger as below:

- Communication:100 Mbit Ethernet

- Inverter communication RS 486, 10/100 Mbit Ethernet

- PC-communication10/100 Mbit Ethernet

- Data interface Modbus TCP

- Ambient temperature-20°C to +55°C

- Relative humidity5% to 95% (not condensate)

- Memory:1 GB

- Internal 8 MB

- External1 GB (SD Card)

#### Meteorological Measurement Stations

The Plant shall be provided with two (2) meteorological measurement stations to monitor ambient temperature, module temperature and the irradiation via pyranometer with respect to the below mentioned meteorological parameters. Additional to the three meteorological measurement station a wind velocity and direction sensor, a precipitation rate sensor and four (4) irradiation sensors shall be installed.

The Contractor is responsible for the installation of the meteorological measurement stations with a minimum timeframe of four (4) weeks before commissioning (to ensure correct calibration and operation of the system) of the Plant.

The meteorological measurement stations shall be able to upload weather information to a web portal at least every 15 minutes (values for every minute).

Each meteorological station shall be installed by the Contractor in a location where no shading is expected from any building, light pole or any other obstacle on the pyranometer or from the meteorological station on the modules of the PV field. The installed stations shall comply with the guidelines of the World Meteorological Organization (WMO).

All stations shall be wirelessly connected to the PCMS system and shall be made available in the PCMS web portal to download collected weather data.

The power supply for meteorological measurement stations and other sensors shall be provided from the PCMS power supply incl. UPS.

There shall be two (2) meteorological stations installed within the Plant. The following measurements shall be provided separately for every meteorological measurement station:

- Global solar irradiation parallel to the modules (20°) in an inclined plane

- Pyranometer (ISO-9060 certification “Secondary Standard”)

- Metering range: 0 to 3,000 W/m²

- Overall accuracy: ± 2 % of metered value (daily average)

- Spectral range 310 to 2,800 nm

- One (1) pyranometer per station

- Including ventilation unit to minimize rain and dust impact

- Anemometer and Wind Vane

- Metering range for velocity 0.2 to 35 m/s

- Metering range for direction: 0 to 360°

- Module temperature and ambient temperature

- Overall accuracy: ± 0.5 °C

- Metering range: - 40 to + 70 °C

- Response time: 20 s (T90)

- PT1000 or PT 100 adhesive foil resistor in 4 wire measuring technology

- At least 3 independent sensors shall be installed in the field,

- State of the art technology to mount the temperature sensor to the module shall be used.

- Precipitation Rate Sensor

- Metering Range: 0 to 10 mm

- Overall accuracy: ± 3 %

- The Contractor shall also provide irradiation and module temperature measurement sets (reference cell) in two (4) locations

- Reference cell (same technology as used in photovoltaic Plant)

- Metering range: 0 to 3,000 W/m2

- Overall accuracy ± 5 % of metered value

- Cell temperature sensor to compensate temperature effects

- One set shall consist of 2 reference cells mounted on bottom and top of a module table

- At least two independent reference cells shall be installed per set

- The measurement shall be logged in the Data Logger as follows:

- The data logger shall be time synchronized

- Data Storage Space: At least 1 GB per station

- Internal Memory: 4 MB

- Keyword protected web application for the Employer/Engineer

- Ambient temperature: -10 to 55 °C

- Data logger shall be compatible with the extreme climatic conditions

- Each data logger shall be equipped with a UPS.

- Web Portal

The PCMS should be capable of uploading all electrical parameters into a web portal. It shall be able to generate graphs and tables from data of all installed devices like inverters, DC combiner boxes, meteorological stations and sensors, etc. and shall support data download as .csv or excel file. Data record to be downloaded shall be 15 minutes interval. It shall include a remote access to e.g. reset curtailment and shut down electrical equipment like inverter. The system shall be able to send alerts to defined email addresses and shall notify the responsible operator. Besides that all alarms including system alarms and important events shall be listed up on the display and the web portal. The lists shall be in chronological sequence showing:

The precise date and time with the specified resolution in actual sequential of events

- Clear text/denomination of alarms and events

- Status message (open, close, off, high, low)

- Sorting of alarms per sub group shall be possible.

All communications equipment shall support Simple Network Management Protocol (SNMP) as well as Remote Monitoring (RMON) functionality for remote management or web interface for configuration and remote management.

The supplied system shall also support data and voice communication uplink facilities.

- Tariff Energy Metering

The PCMS shall be linked to the energy metering panels in the plant’s substation and in the control building. The PCMS shall be collected the data of export meter, import meter and VAR meter.

- Codes and Standards

All deliveries and works shall meet or exceed applicable requirements set forth by the latest edition of the following international and national codes and standards. In addition, all local rules and regulations shall be strictly adhered in all respects. Among others:

- ISO 11801 Generic cabling for customer premises

- ISO/IEC 12207 Software testing, integration and documentation

- IEC/TR 62541 OPC Unified Architecture – all parts

- IEC 61508 Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems

- ANSI/IEC 60529 Degrees of Protection Provided by Enclosures (IP Code)

- IEC 60950-1 Information technology equipment. Safety; Part 1-General requirements; Safety aspects (specific Clauses)

- ISO 10026 Open Systems Interconnection (or ISO/IEC 10026)

- ISO 9241 Ergonomics of human-system interaction

- ISO 11064 Ergonomic Design of Control Centers

- ISO 27002 Cyber Security

- IEC 62381 Ed.2 Automation systems in the process industry – Factory acceptance test (FAT), site acceptance test (SAT), and site integration test (SIT)

- IEC 62337 Ed.2 Commissioning of electrical, instrumentation and control systems in the process industry - Specific phases and milestones

- DIN EN 62337:2011-01 Commissioning of electrical, instrumentation and control systems in the process industry - Specific phases and milestones (IEC 65E/166/CDV:2010);

- ISO/IEC 25010 Systems and software engineering. Systems and software quality requirements and evaluation (SQuaRE). Systems and software quality models (2011)

- EN 50130-4 Electromagnetic compatibility; Product family standard: Immunity requirements for components of fire, intruder and social alarm systems

- EN 50136 Alarm transmission systems and equipment

- IEC 60617 Graphical symbols for diagrams

- IEC 60947 LV Switchgear and control gear

- IEC 61000 Electromagnetic compatibility (EMC)

- IEEE 802 series Standards for Local and Metropolitan Networks

- ISA 99 Security for Industrial Automation and Control system

Regarding the communication gateways between the Plant and the National Control Centre IEC-870-5-101 implementation protocol shall be used.

(E) Remote control via Telephone Modem or mini web server.

### 2.11.10 DC, UPS & Auxiliary Power Supply

The Bidder shall supply, all requested auxiliaries (but not limited to), such as:

- UPS Battery Emergency Power Supply (DC and Safe AC)

- internal/external lighting and emergency lighting systems in Control building

- power supply of CCTV

- fire alarm system

The Bidder shall submit the proposed auxiliary supply system with his Proposal.

Power supply systems may be categorized into essential and non-essential groups. Essential supplies should be continuously available without any interruption, whereas non-essential ones may be allowed to be subject to interruptions.

Low-voltage AC and DC systems shall be designed in accordance with the IEC 60364.

###### DC and Safe AC

The uninterruptable power supply system (UPS) shall serve the costumers which have to remain in operation in the event of the network failure i.e. emergency lighting, measuring, control room, CCTV, fire alarm system etc.

Some equipment (e.g. MV switchgear circuit breaker heaters) may require the provision of changeover power supplies.

The 100% load of 230/400 V AC (Safe AC), 220 V DC and 24 V DC are to be defined by the Contractor providing classification of consumers and their required backup time values.

The UPS system shall consist of:

- rectifier/battery/inverter set

- static switch by-pass and maintenance by-pass set

- three phase AC distribution board.

The DC system shall consist of:

- AC/DC rectifier

- batteries

- DC distribution board.

The rectifiers and inverters shall be arranged in sheet steel cubicles, which shall be matched to the distribution cubicles in respect of height and other dimensions.

The rectifiers and inverters shall be designed for operation with natural cooling. If forced air-cooling is required, then 2 x 100% air fans with monitoring and local and remote alarm signals must be provided.

The DC distribution is to be fed by 1x100% batteries and rectifier.

The digital control system (DCS) shall be supplied from a 24 V DC system. Redundant 24 V DC distribution system shall be provided.

The cubicles of 24 V DC consumers shall be supplied by redundant feeders. Redundant Safe AC system shall be provided.

230 V Safe AC system comprises one inverter with static bypass switch unit and a safe busbar. The inverter shall be supplied from sections of the 220 V DC main distribution. The static bypass switch shall be supplied from the 0.4 kV essential switchgear.

The 230 V Safe AC system supplies the equipment requiring uninterrupted supply (UPS) e.g. measuring, control system etc.

The 220/24 V DC/DC converters serve as supply for I&C cabinets and other consumers requiring 24 V DC supply. Each DC/DC converter is supplied via coupling diodes from both sections of the 220 V DC main distribution.

The outgoing circuits in the safe DC and AC main distribution shall be equipped with monitored fuse- and load-break switches, fuses and contactors, mini-circuit breakers, etc.

The individual cubicles shall be bulk headed against one another by sheet metal walls or equivalent material.

The DC UPS shall be located inside an air-conditioned room, the rectifier / charger and distribution board shall be rated for continuous operation at 40° C.  Sizing of battery shall be based on a minimum of -3° C and maximum of 55° C ambient.  The temperature derating factor and ageing factor of the battery shall be based on the above temperatures.

###### Battery

For the DC system, the Bidder shall supply Valve-Regulated Lead Acid (VRLA) batteries type batteries designed according to Standard EUROBAT 15 with a life expectancy of 15 years or more.

The batteries shall be sized such that with each (1x100%) battery supplies the total load and shall be able to cover 100% load for 3 hours.

Sizing of batteries shall be based on worst case scenarios that might cause a total loss of AC services (i.e. total blackout, fault on a major bus in the installation, etc.). As a minimum, the DC batteries shall have enough capacity to trip breakers and switches at the beginning of the discharge period, to supply power to the continuous DC load and to close the elements of the installation that will restore AC services.

If applied, battery banks with exposed live parts shall be kept in a room or cubicle accessible only to authorized personnel.

Battery rooms or cubicles shall be dry and adequately ventilated to limit hydrogen accumulation. Allowable hydrogen levels and recommended number of air changes shall conform to national regulations.

Batteries shall be installed on insulated subframes with the necessary consoles and fixed material. At least 1.0 m access space shall be provided at the front and sides of the battery rack.

###### Internal/external lighting and emergency lighting system

The installation method differs between internal lighting (offices, rooms for similar purposes, technical rooms) and exterior lighting.

All lighting fittings and all equipment comprising the lighting sub-distribution units shall meet the operational requirements in full at an ambient temperature of 40°C and for a relative humidity of up to 100%.

The lights must be connected in a 3-phase circuit, so that in an event of failure of the phase only each third lamp will go out. The cable cross section shall be calculated according to the IEC 60364-5-52.

Location of the lighting and small power equipment shall be reviewed before installation so that satisfactory co-ordination with walkways, streets, fences, gates, crossings, entries, PV panel support structures, cable ways and other installations can be assured.

The lighting systems are to be classified as follows:

- Normal lighting fed from normal supply: shall provide desired and required illumination levels in the various indoor and outdoor areas and roads

- Emergency lighting fed from safe AC supply (UPS): In case of failure of normal lighting, emergency lighting shall provide sufficient illumination to allow safe movement of personnel.

In coordination with the design of the alarm and CCTV systems outdoor lighting as a minimum shall be provided for perimeter of the plant and at the entrances of all buildings on site including the transformer stations.

Indoor lighting can be operated manually and/or using automatic motion detecting devices where suitable.

In control room, switchgear rooms flush-mounted fluorescent tube fittings are to be provided. The lightning fittings are to be designed with required louvers for mounting in the suspended mineral fiber acoustic tiles.

In battery room explosion-proof lighting fitting (EExd II CT2) are to be provided.

Outdoor lighting at the entrances of buildings and where suitable shall be operated automatically (motion detection) and also shall permit remote control from the main control room and shall be included in the concept for intrusion alarm. The perimeter lighting shall be operated centrally and also included in the security concept for the plant.

The lighting shall be designed so that the lighting illumination density listed in DIN EN 12464-2 will be achieved. In that respect an aging factor of 20 % is to be considered so that new lighting densities must be achieved as a minimum in the acceptance measurement.

###### Fire alarm system and fire fighting

The detectors shall be stable against environmental influences (ambient temperature, humidity etc.) and shall be so positioned as to avoid the possibility of spurious operations due to air current from pressurization, ventilation or air-conditioning grills.

A manually operated alarm system shall be provided in each building with an alarm initiating point at each room exit. This system shall be fully integrated with the automatic fire detection and alarm system.

Alarms shall be signaled locally (audible and visible) and in the plant control room and should also permit remote connection.

All MVAC systems must be shut down in case of fire to prevent spread of fire.

Suitable firefighting equipment shall be provided in the control buildings, transformer stations, and transformers compounds as required.

- The design and installation of the fire protection and alarm systems shall be in accordance with Section 6.2.4;

- The design and installation of the fire protection and alarming systems shall be in accordance with highest international recognized standard, preferably the relevant NFPA-Codes and international standards

The fire detection and alarm shall be DC operated by UPS

All fire equipment & system installed outdoor must be IP65.

### Protection and Control System

For standardization of operating performance and facilities and spare requirements, the protection relays to be supplied under this project shall comprise Alstom (UK)/(France), ABB (Switzerland/Sweden) and Siemens (Germany) make manufacture or equivalent standard quality.

The protection shall be sufficiently sensitive to cater for the minimum fault level condition. This will be advised later. The protection shall also be suitable for a system fault level minimum to the switchgear rating of 25kA (11kV). All current transformer design shall be based on these fault levels.

- All relays shall operate correctly within system frequency limits of 47Hz to 51Hz.

- Installation, testing and commissioning of all protective relays shall be done by the Protetive Relay Engineer(s) of the relay(s) manufacturer(s). The manufacturer(s) Engineer(s) shall also provide on-site, local training of 2 weeks duration to ten (10) BPDB Engineers on protection schemes and protective relays. All costs for the above shall be deemed to be included in the contract price.

11 kV system overall fault clearance times (i.e. from fault initiation to arc extinction) shall not exceed the following:

| Type of Fault | Maximum Fault Clearance Time |
| --- | --- |
| Substation and Transformer fault | 100 msecs |
| Line fault |  |
| (a) Up to 72% of the line length (i.e. 90% of a distance relay Zone 1 reach setting of 80% of the line impedance) | 100 msecs |
| (b) 72% to 100% of the line length | 130 msecs plus protection signaling time. |

These requirements must be fulfilled under all system conditions including maximum dc current offset and include any time delay caused by the use of capacitive voltage transformers. Clearance within these times shall be achieved for all types of faults except high resistance earth faults detected by DEF protection or under circuit breaker failure conditions.

Control and relay equipment shall be mounted on panels and cubicles as specified and shall be installed in permanent buildings on the substation sites. Except where otherwise specified, control panels shall be segregated from metering and protection panels. Separate protection panels shall be provided for each feeder circuits.

Panels provided as extensions or for erection in the same room as existing panels shall be of similar design and appearance to those existing. Equipment, meters, etc., mounted on such panels shall likewise be of style and scaling similar to the existing equipment. Characteristics of relays, etc., and all connections of equipment to be associated with existing equipment shall be such that they are fully compatible with and can operate satisfactorily in conjunction with the existing equipment. The characteristics and appearance of all such equipment shall be to the approval of the Employer.

Control panels shall incorporate all necessary control and indication facilities for the operation of the plant and equipment at the associated substation. Protective relays and control equipment which have communication capabilities with fiber optic interfaces built-in would be prefer-red so that in future they can communicate with the Station Monitoring system and can easily be integrated into Substation control systems.

connected through the concept of Earth Mats for interconnection with separate earth pits.

### 2.11.12 Static Var Generator

The Static Var Generator (SVG), is a reactive power compensation system, used for compensation of normal or dynamic three-phase, balanced or unbalanced loads. Some of the important highlights of SVG are as follows

- Stable reactive power compensation for capacitive, inductive, positive sequence, negative sequence and zero sequence loads

- Rapid dynamic responses, stable parameters & high precision of reactive power compensation

- High efficiency, low thermal loss and advanced ECO mode achieve intellectual energy saving

- Modular design offers a variety of coordination with various compensation capacities

- The system adopts an advanced 3-level structure & consists of digital signal processors (DSP), large programmable controllers & high-power electronic devices, which has excellent performance and superior reliability

- Supports remote power on/ off functions via computer monitoring

The SVG system is composed of a fixed-type SVG module, a door mounted display monitor and an SVG system cabinet. The external CT is used for the detection of load current and extraction of reactive power that needs compensation, based on which, the SVG controller controls the main power circuit to generate reverse reactive current in this way, the load- carrying reactive power is counteracted.

Each standard SVG system cabinet can be connected to up to 7 modules in parallel. As for the non-standard cabinet, the quantity of the modules installed inside could be varied according to final rating required. The Display Monitor is used for monitoring and controlling the SVG module online.

Some of other SVG Features as follows:

- SVG has high reactive power compensation accuracy

- SVG can correct both Leading & Lagging PF

- Fast response to Dynamic load variations

- Complete response time (from reactive power generation to elimination) of SVG is less than 20ms (1 cycle), with instant response time of < 100 micro sec. which enables SVG to improve Power Factor for fast changing dynamic loads

- SVG capacity increase in pace with load changes

- High adaptability, reliability and stability

- For harmonic filtration, the SVG can be complimented with tuned filter banks of 3rd, 5th, 7th & other as per network requirement

- SVG ambient temperature: -10°C to +50°C

- Input voltage range: 11kV, 50/60Hz ±10%

- SVG is not affected by harmonic currents

- The SVG is completely modular in structure. Each module can work independently, and modules can be paralleled to increase the capacity

- Active compensation technology avoids harmonic resonance

- Actual output capacity is the same as rated capacity

- The following information must be mentioned in Static Var Generator:

- Name of the manufacturer of Static Var Generator.

- Month & Year of manufacture.

- Country of origin.

- Rated Voltage and Input Voltage Range.

- Rated Capacity per module and per cabinet.

- Reactive Power, Imbalance correction.

- Response time, thermal loss.

- Switching frequency, controller communication, monitoring

- Physical specification and dimension

- Unique serial No and Model No of the Static Var Generator.

- Date and year of obtaining IEC qualification certificate.

- Name of the test lab issuing IEC certificate.

- Other relevant information on traceability of certifications.

Characteristics

- Static Var Generator (SVG) utilizes three level inverters topologies to provide real time response to reactive power requirements and load balancing. It monitors the current continuously and compensates the reactive part of the measured current.

- 3MVAR, 3P4W (3-phase/4-wire) device for phase current and neutral wire correction.

Safety features

- Overload protection

- Internal short-circuit protection

- Overheating protection

- Overvoltage and under voltage protection

- Inverter bridge protection

- Resonance protection

- Fan fault alarm

### 2.11.13 Fire Fighting System

General:

The Contractor shall design, manufacture, delivery to the Site, install, test and commission the firefighting system to protect the Solar PV Plant and all associated equipment and Outdoor yard. Fire detection and Alarm system for office building and control & equipment room shall be provided. In particular, the following shall be included:

- Dry Chemical Powder Fire Extinguishers.

- Water Hydrant System including electric motor, water reservoir, hydrant stands, hoses etc.

- Sand Buckets

- Fire Detection and Alarm system

Design Requirements:

All fire protection installations shall comply with the requirements of the codes of practice of the National Fire Protection Association, Boston, Massachusetts, U.S.A as appropriate for the respective systems, subject to the approval of the Engineer. The codes and practice of the Japanese Fire Protection may also be considered.

Dry Chemical Powder Fire Extinguishers:

The Dry Chemical Powder Fire Extinguisher shall be Upright type of capacity 8 Kg conformed to NFPA Codes and Standard. The fire extinguisher shall be suitable for fighting fire of oils, solvents, gases, paints, varnishes, electrical wiring, live machinery fires, all flammable liquid & gas.

The following portable firefighting equipment or equivalent shall be provided:

(1) 	Five Nos 5 kg Dry chemical extinguishers

(2)	Ten nos. 10 kg Dry chemical extinguishers.

Water Hydrant System:

- Fire hydrant of water type shall be provided in the power plant.

- The source of firefighting water supply system for the site shall be firefighting water tanks with the needed capacity which shall contain adequate water supply for firefighting.

- Calculations for Firefighting water reserve and pumps (with electrical motor and engine driven) shall be carried out by the Contractor and justify the fulfillment of these requirements to local standards as well as international standards.

- Each hydrant stand shall be fitted with an isolating valve and approved type of instantaneous hose complying 30-m hose with combined jet/water-fog nozzle shall be provided in the cabinet adjacent to each hydrant.

Sand Buckets:

The bucket should be wall mounted made from at least 24 SWG sheet with bracket fixing on wall conforming to NFPA Codes and Standard.

Fire Detection and Alarm system:

Fire detection shall be by means of ultra violet flame detectors with a backup system utilising rate-of-rise temperature detector. The use of smoke detectors shall be subject to specific approval by the Engineer as regards their type and location.

### Security and Surveillance

General:

The Contractor shall design, manufacture, delivery to the site and install Communication and Security System which shall be comprised of but not limited to the following:

- Closed Circuit Television (CCTV) System (IP based) for the plant security;

- One IP telephone set (Cisco) with accessories.

Closed Circuit Television (CCTV) System:

Security and surveillance of different operating areas in the plant as an aid to operators, IP based CCTV system shall have to be provided. Adequate number of dome type cameras with facilities like Zoom, pan, tilt etc. would be provided at various operating areas.

The camera shall have a resolution of at least 1280 horizontal lines. The camera pictures shall be displayed at the Administrative Building (Manager), Central Control Room (CCR) and Security Supervisor room where the camera view or combination of views, selected by an operator shall be displayed on colour LCD video monitors. A digital video recording system shall also be provided to allow a permanent record to be made from all or selected channels. The system shall store the CCTV data for at least 1 (one) month.

The complete system, as specified including, but not limited to the following: -

- High resolution color cameras including lenses, mountings and housings.

- Camera for CCTV have capabilities to cover capturing outdoor video ranging minimum 30 meter.

- Color Monitors

- Pan/tilt units for moveable cameras

- Video matrix switcher and control system

- Hard Disk / DVD recorder

- Video multiplexers

- Video transmission system including cabling, launch, line, equalizing, repeating amplifiers, etc.

These specific areas as listed below shall be considered as minimum requirements. As minimum, the following areas of the plant shall be covered by video surveillance (CCTV).

- Control Room (4 Unit)

- Building gate entrance area. (2 Unit)

- Security gate (2 Unit)

- Sub-station (2 Units)

- Solar PV Array area (Minimum 50 Units)

### 2.11.15 Emergency Diesel Generator

One (1) set of emergency diesel generating set and associated equipment shall be installed at the power plant. The capacity of the EDG shall not be less than 1250 kVA [pf 0.80] for supplying power to : (i) the pumping stations, (ii) street light including emergency lights, (iii) control room after UPS backup, (iv) deep tube well, (v) firefighting system, (vi) AC system in the control room, and (vii) any other emergency load as well as to supply power to the consumer during low power generation from the solar power plant for continuous operation of the plant.

EDG shall be of automatic starting system [compressed air/ Battery] including quick start & loading capability. The starting system shall be capable of carrying out at least five (5) consecutive starts without auxiliary power supply. In case of power failure in 0.4 kV bus, EDG will start and supply power to 0.4 kV emergency bus in auto mode. EDG synchronizing facility with 0.4 kV live bus is also required.

EDG is required for the safe shutdown of the plant/ equipment under emergency condition and in case of power failure for certain essential applications like battery chargers, emergency lighting and all auxiliaries necessary for safe coasting down of equipment and turning gear/ barring operation of the turbines.

EDG shall have diesel storage capacity for minimum 15 days of continuous operation in full Load.

### 2.11.16 Weather Station/ Meteorological Measurement Station

The Plant shall be provided with two (2) meteorological measurement stations to monitor ambient temperature, module temperature and the irradiation via pyranometer with respect to the below mentioned meteorological parameters. Additional to the three meteorological measurement station a wind velocity and direction sensor, a precipitation rate sensor and four (4) irradiation sensors shall be installed.

The Contractor is responsible for the installation of the meteorological measurement stations with a minimum timeframe of four (4) weeks before commissioning (to ensure correct calibration and operation of the system) of the Plant.

The meteorological measurement stations shall be able to upload weather information to a web portal at least every 15 minutes (values for every minute).

Each meteorological station shall be installed by the Contractor in a location where no shading is expected from any building, light pole or any other obstacle on the pyranometer or from the meteorological station on the modules of the PV field. The installed stations shall comply with the guidelines of the World Meteorological Organization (WMO).

All stations shall be wirelessly connected to the PCMS system and shall be made available in the PCMS web portal to download collected weather data.

The power supply for meteorological measurement stations and other sensors shall be provided from the PCMS power supply incl. UPS.

There shall be two (2) meteorological stations installed within the Plant (north, center south). The following measurements shall be provided separately for every meteorological measurement station:

- Global solar irradiation parallel to the modules (20°) in an inclined plane

- Pyranometer (ISO-9060 certification “Secondary Standard”)

- Metering range: 0 to 3,000 W/m²

- Overall accuracy: ± 2 % of metered value (daily average)

- Spectral range 310 to 2,800 nm

- One (1) pyranometer per station

- Including ventilation unit to minimize rain and dust impact

- Anemometer and Wind Vane

- Metering range for velocity 0.2 to 35 m/s

- Metering range for direction: 0 to 360°

- Module temperature and ambient temperature

- Overall accuracy: ± 0.5 °C

- Metering range : - 40 to + 70 °C

- Response time : 20 s (T90)

- PT1000 or PT 100 adhesive foil resistor in 4 wire measuring technology

- At least 3 independent sensors shall be installed in the field,

- State of the art technology to mount the temperature sensor to the module shall be used

- Precipitation Rate Sensor

- Metering Range: 0 to 10 mm

- Overall accuracy: ± 3 %

- The Contractor shall also provide irradiation and module temperature measurement sets (reference cell) in two (4) locations

- Reference cell (same technology as used in photovoltaic Plant)

- Metering range: 0 to 3,000 W/m2

- Overall accuracy ± 5 % of metered value

- Cell temperature sensor to compensate temperature effects

- One set shall consist of 2 reference cells mounted on bottom and top of a module table

- At least two independent reference cells shall be installed per set

- The measurement shall be logged in the Data Logger as follows:

- The data logger shall be time synchronized

- Data Storage Space: At least 1 GB per station

- Internal Memory: 4 MB

- Keyword protected web application for the Employer/Engineer

- Ambient temperature: -10 to 55 °C

- Data logger shall be compatible with the extreme climatic conditions

- Each data logger shall be equipped with a UPS.

### 2.11.17 Distribution System

Distribution Line components as per BPDBs’ Standard. Contractor must follow this.

Distribution System of Bhasanchar comprises of 11 kV Line, 11/0.4kV line, 0.4kV LT line and associated Distribution Transformer & Energy Meter

- Distribution Line

1.0 General

This section of the document includes the design, manufacture, testing & inspection of 11kV, 11/0.4kV & 0.4kV Distribution System Materials as specified.

1.01 Climate Data

Main climate data that must be considered for the goods will be the followings:

| Climate | : | Tropical, intense sunshine, heavy rain & humid. Maximum humidity and temperature sometimes occur simultaneously. |
| --- | --- | --- |
| Maximum Temperature | : | 45-degree C |
| Minimum Temperature | : | 03-degree C |
| Average daily Temperature | : | 30-degree C |
| Average isokeraunic level | : | 80 days/ year |
| Relative humidity | : | 50-100% |
| Average annual rain falls | : | 3454 mm |
| Maximum wind velocity | : | 200 km/ hour |
| Altitude | : | 300 meters above Sea level |
| Atmospherically, Mechanical and Chemical impurities | : | Moderately polluted |

The information is given solely as a guide for Tenders and no responsibility for its, accuracy will be accepted not will any claim based on the above be entertained.

Materials supplied under this contract will be installed in tropical locations that can be considered hostile to its proper operation. Particular problems that shall receive special consideration relate to operation in a hot humid environment and presence of the insects and vermin.

1.02 System Particulars

| SL. NO. | SYSTEM CHARACTERISTICS | VOLTAGE LEVEL |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Normal System Voltage, KV (Voltage Class) |  | 2 3 0 | 1 3 2 | 3 3 | 1 1 |
| 3. | Maximum System Voltage, KV |  | 245 | 145 | 36 | 12 |
| 4. | System Frequency, Hz |  | 50 | 50 | 50 | 50 |
| 5. | Phase Rotation (Clock wise) |  | R S T | R S T | R S T | R S T |
| 6. | Type of System Grounding | Solid |  | Solid | Solid | Solid |
| 7. | Rated Fault Level (3-Phase Symmetrical), MVA 3 sec. | 1 2 5 5 0 |  | 6 0 0 0 | 1 5 0 0 | 3 8 1 |
| 8. | Basic Insulation Level, KV |  | 750 | 650 | 170 | 75 |
| LOW VOLTAGE 415/ 240V CHARACTERISTICS: |  |  |  |  |  |  |
| 9. | Normal System Voltage, V (Voltage Class) | 415/ 240 |  |  |  |  |
| 10. | Type of System Grounding | Solid |  |  |  |  |

High voltage current carrying equipment should be capable of carrying the three phase fault levels for a period of three second.

1.03 List of Materials

| Sl. No. | Description of Materials |
| --- | --- |
| 1. | Steel Pole (12M, 350DaN & 450DaN; 9M, 200DaN & 300DaN) |
| 2. | Pole Fittings (Cross Arm, 5-Spool Rack & Guy Set) |
| 3. | ACSR Dog, AAC WASP (Insulated), AAC ANT (Insulated) Conductor & Guy/Earth Wire |
| 4. | Insulator (Pin, Disc, Shackle & Guy Insulator) |
| 5. | Line Accessories (Mid span joint, PG Clamp, H-type connector, Preform termination, Armor rod, Binding wire, etc.) |
| 6. | 11/0.4kV 3-P Distribution Transformer (250KVA, 100KVA & 50KVA) |
| 7. | 6.35/0.23kV 1-P Distribution Transformer (10KVA) |
| 8. | Transformer Platform for 3-P Transformer |
| 9. | Clamp for 1-P Transformer |
| 10. | Drop Out Fuse Cut out (DOFC), Lighting Arrester (LA) & MCCB for Distribution Transformer |
| 11. | Side mount bracket for DOFC & LA for 1-P Transformer |
| 12. | LV PVC Copper Cable for Distribution Transformer |

## 1.04 Design, Supply, Erection, Installation, Testing and Commissioning of 11kV, 11/0.4kV and 0.4kV Overhead Distribution Lines:

(Not limited but at least the following works to be done by the turnkey contractor)

- The Contract shall cover the following works unless otherwise specifically mentioned in the Specifications.

a)	The work includes the alignment, measurement of angles, location of the center line of the route (along the nearest road), the boundaries of the right of way of each structure, location of the pole position on Mouza Map including collection of Mouza Map, making final alignment of the line on Mouza Map, preparation of Profile Map & Staking Sheet (existing & proposed) and a list of affected land owners (if any) with areas falling within the right of way.

b)	Clearing the right of way of shrubs, trees, bamboo and structures for a distance of 2 meter on either side of the line.

c)	Supply and Installation of line materials with all accessories to be newly constructed under the contract.

d)	Testing, commissioning and documentation (as built drawing) of all lines.

- Design, Manufacture, Supply, Installation/Erection, Construction, Testing and Commissioning etc. of the following works are the scope of works:

1.	Detailed Survey

a) The work includes theodolite & leveling survey of the alignment, measurement of angles, location of the center line of the route.

b)  Clearing the right of way of shrubs, trees, bamboo and structures for a distance of 2 meter on either side of the line.

i)  Trimming of tree branches adjacent to an O/H line

It includes cutting, trimming and stacking of tree branches over or within a radial distance of 2 meter of the overhead line and return of the tree branches to the owner or their removal of a recognized refuse area with payment of compensation to the owner.

ii)  Tree cutting and uprooting

It  includes  cutting  and  uprooting  of  a  complete  tree  by  excavating  soil around the tree to a depth of at least 0.5 meter and cutting through the tree trunk below ground level, top looping of tree as required before falling the safe lowering of the tree to the ground away from any line or building or other structure, the cutting upto transportable size, stacking and handing over to the owner or if not required by the owner, removal to recognized refuse area, the back-filling and ramming of the excavation with soil imported by the contractor and payment of compensation to the owner.

2.	Poles

Supply and installation of 12 meter and 9-meter Steel Poles, complete in all respect.

a)	Erection of Poles

Pegging of pole position for approval of the engineer, excavation of earth in all kinds of soil including pucca breaking if  required  to  form  a  hole  as  per reference  drawing of BPDB,  preparation  of  concrete  base  (if  required). Average pole to pole span for 11kV, 11/0.4kV & 0.4kV overhead line shall be maximum 35 meter.

b)	Concrete muffling (only for section pole)

It includes all materials required at site, excavation of earth in all kinds of soil including pucca breaking if required and installation of suitable framework. It also includes the supply of concrete material (1:2:4 – cement: sand: Khoa) and pouring of concrete as per reference drawing of BPDB, backfilling and ramming of excavation and disposal of surplus soil.

c)	Installation of Cradle-guards (where necessary)

It includes the assembly of cradle guard and its installation with pole attachments as per reference drawing of BPDB.

d)	Painting of pole number and danger marking

It includes painting of old number, if required, preparing pole for painting, painting of background, painting of new pole number (black) and danger sign (red) as per reference drawing of BPDB. It also includes supply of all paint (oil base) and painting tools of best quality.

3.	Cross Arms

Supply and installation of Cross Arms with accessories, complete in all respect.

a)	Installation of Cross Arms

It includes assembly and fixing of complete cross-arms with pole clamps as the case may be to the installed poles in various combinations according to reference drawings of BPDB. Each combination consists of one three phase three wire for 11kV set.

4.	5-Spool Wire Rack

Supply and installation of 5-Spool Wire Rack with accessories, complete in all respect.

a)	Installation of 5-Spool Wire Rack

It includes assembly and fixing of complete rack with pole clamps as the case may be  to  the  installed  poles  in  various  combinations  according  to reference drawings of BPDB. Each combination consists of one three phase four wire for 0.4kV set.

5.	Guy Assembly

Supply and installation of Guy Assembly with Guy wire, Guy insulator & other accessories, complete in all respect.

a)	Installation of Guy Assembly

Excavation of an undercut and slotted guy pole as per drawing assembly, installation of guy rod, guy insulator, guy wire, pole fittings, guy preform & other accessories, backfilling and ramming of the excavation, installation, tensioning and making off of the guy wire to guy rod & pole to adjust the correct tension after erection of the line conductors (as per attached drawing of BPDB).

b)	Installation of horizontal Guy Assembly (flying stay) including fly pole (if required)

Excavation of an undercut and slotted guy pole as per drawing assembly, installation of guy rod, guy insulator,  guy  wire,  pole  fittings  &  other accessories, backfilling and ramming of the excavation, installation, tensioning and making off of the guy wire to guy rod & pole to adjust the correct tension after erection of the line conductors (as per attached drawing of BPDB).

5.	Insulators

Supply and installation of Insulators with accessories, complete in all respect.

a)	Installation of 11KV Pin Insulators

It includes assembly and installation of one three phase set of 11KV Pin Insulators with fittings to installed poles according to reference drawings including binding & fixing of conductor to insulator.

b)	Installation of 11KV Disc Insulators with fittings

It includes assembly and installation of one three phase set of 11KV Disc Insulators with Fittings to installed poles according to reference drawings including binding & fixing of conductor to insulator.

c)	Installation of LT Shackle Insulators

It includes assembly and installation of one three phase set of Shackle Insulators with fittings to installed poles according to reference drawings including binding & fixing of conductor to insulator.

6.	Overhead Conductor & Earth Wire

Supply and installation of Conductor & Earth Wire with accessories, complete in all respect.

a)	Installation of overhead conductor and earth wire

It includes laying out and stringing of one conductor including the fitting of conductor drum on the jacks, lifting into snatch blocks, pre-tensioning, tensioning and sagging of conductor, setting of conductors to correct position on insulators, making off at terminations, binding with insulators and jumpering of the conductor. New conductors must be pre-tensioned for a period of not less than one hour at a tension equal to one third of the breaking load of that conductor.  Tensioning must be carried out  by  using  straining  device  in  a manner approved by the Engineer.

b)	Installation of Mid Span Joints and Repair Sleeves (as and where applicable)

It includes cutting, clearing and de-oxidizing the conductor ends, installing and making a mid-span joint during the erection of new conductor.

c)	Installation of Compression connectors (as and where applicable)

It includes installation and compression jointing of one compression connector including cutting, forming and clearing of jumper and its connection to the line.

d)	Installation of Armour Rod, Binding wire (as and where applicable)

It includes installation of one set Armour Rod for binding each conductor with the insulator set.

e)	Installation of overhead conductor and earth wire for river crossing (if applicable) It includes laying out and stringing of one conductor including the fitting of conductor drum on the jacks, lifting into snatch blocks, pre-tensioning, tensioning and sagging of conductor, setting of conductors to correct position on insulators, making off at terminations, binding with insulators and jumpering of the conductor. New conductors must be pre-tensioned for a period of not less than one hour at a tension equal to one third of the breaking load of that conductor.

Tensioning must be carried out by using straining device in a manner approved by the Engineer.

2.0 Technical Specification of STEEL POLE

Standards:

The Steel Pole as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the Steel Pole shall be in accordance with the followings or equivalent International standards.

BS        729 : 1971	Hot dip galvanized coating on iron and steel articles or equivalent.

BS	4190 : 1967	Isometric hexagonal Bolts, Screws and Nuts.

BS	4360		Specification for weld able Structural Steel

BS	4870		Specification for approval testing of welding procedures.

BS       5649  : 1982	Part 4 Recommendations for surface protection of Metal Lighting columns.

BS	5750  : 1997	Quality System

BS	6323		Part 1 to 8 for steel tubes.

ASCE/48-05               Design of Steel Transmission Pole Structures

If the Bidder offers other equivalent standards, full details including copies in English Language of such standards shall be submitted with the offer.

Specifications:

The Steel Poles shall be of the following types:

- Telescopic, uniformly tapered circular/polygonal cross-section, in more than one section.

The poles shall have 2 (two) sections for 9 Meter, 12 Meter Poles and 3 (three) sections for 15 Meter Poles. For all the above types of poles, no welding is allowed after galvanization.

The Bidder shall submit the offer with materials required which shall meet the standard and specification as specified. The Bidder shall submit all the technical data as required in the Guaranteed Technical Particulars for each type of pole.

All information including design calculation, drawings, catalogues, materials standard, welding procedure and standard, fabrication and erection procedure shall be provided along with the tender.

Inspection and Testing:

The manufactured items will be inspected at the manufacturer’s plant by the Engineering Team appointed by the purchaser. Test shall be performed in accordance with the relevant standards unless otherwise stated.

Before full scale manufacture is commenced, 3 (three) samples of each type of pole shall be prepared for testing and approval by the engineer. Production items not meeting the same standard as the initial samples approved by the Engineering Team will be rejected.

Definitions and Abbreviations:

The following definitions and abbreviations shall be applied to this specification.

Definitions:

i)     Failure		Inability of the pole when under test to support further load or when                                    			deformation or buckling of the pole renders it unserviceable.

ii)    Longitudinal 	The horizontal direction parallels to the run of the direction of the conductors.

iii)   Transverse	The horizontal direction at right angles to the run of direction of the conductors.

iv)   Ultimate	The strength at which the pole will not accept any further applied force or when deformation or buckling or the pole renders at unserviceable.

v)    Pole Type:

| a) | Telescopic in more than one piece | Assembled from a series of manufactured tapered sections, which are fitted together, and then the total assembly is axially loaded to force the tapered unit’s together thus proving friction connections between sections. The Bidder shall have mentioned the number of sections for each type of pole. The taper shall be uniform throughout the length of the pole. However, the taper ratio for all the sections shall be same. Assembly shall be by means of a simple slip joint without the use of bolts, site welding or other jointing device at time of erection. No circumferential joints are allowed. Jointing shall be designed for a minimum lap of 1.5 times the largest inside diameter of the female section with allowances for fabrication tolerance. |
| --- | --- | --- |
| b) | Stepped Poles | Manufactured from a single length of tube, the diameter being reduced in parallel steps by passing the tube through a series of dies. No circumferential joints are allowed. |

Abbreviations

BS	: 	British Standard.

IEC	:	International Electro-technical Commission.

Mpa	:	Mega Pascal = 1 N/sq. mm

Material and Manufactures.

All materials shall be new and conformed to the relevant standards referred to this specification.

Materials

The minimum yield strength of the materials of pole shall be 280 N/sq. mm as per BS 4360.

Manufacture

All welding of the poles shall be carried out at the manufacturer’s plant and before galvanization. No site welding will be permitted.

Welding shall be carried out in accordance with the procedures of an international standard approval by the Engineer and this procedure shall be tested in accordance with BS 4870 or equivalent standard.

Welds parallel to the longitudinal axis of the poles shall be fillet welds or full penetration butt welds with backing plates. All welds shall be capable of withstanding, without failure of cracking, the stresses in a pole when subject to its ultimate design loads. Only two longitudinal welding is allowed for each section of pole. No circumferential joints are allowed. In case of telescopic poles, no hole is allowed in the overlapping portion for fixing of fitting and accessories.

Dimensional Tolerances:

| i) | The tolerance on thickness | : | - 0% to +10% on each sheet |
| --- | --- | --- | --- |
| ii) | Outside Diameter |  | - 0% to +2% |
| iii) | Length of Sections |  | + 40mm |
| iv) | Telescopic Poles |  | After assembly telescopic poles shall not exceed of their stated length by + 75mm for 9m & 11m poles, +100 mm for 12m poles and +125 mm for 15m poles. |
| v) | Straightness |  | Straightness shall not exceed 1/300 of their height. |
| vi) | Thickness |  | The minimum thickness of the material shall be 3 mm for 9 Meter Poles and 4 mm for 12 Meter & 15 Meter Poles for a length of minimum 3.0 meters section from the bottom level. |
| vii) | Taper/Slope of Poles |  | The side taper of the pole shall be between 15 mm to 25 mm per meter length. |

The design of pole shall be on the basis of minimum values considering tolerance.

Assembly of Telescopic Pole

Each pole shall be assembled in the factory and prior to assembly all seam welds on joint mating surfaces shall be ground flush. All right spots in the galvanizing on mating surface shall be ground and or fired flat and if the galvanizing is damaged it shall be repaired.

During the application of the compressive load to force the sections together, the joints shall be agitated by striking them with timber or rubber mallets or by any other method as approved by the Engineer. The coating of galvanization shall not be damaged by this method of assembly.

Corrosion Protection.

All poles internally and externally are to be hot-dip galvanized in accordance with BS 729: 1971 or equivalent standard or latest revision thereof.

After galvanization of poles the external surface of all poles below ground level and 1000mm above ground level shall be painted as follows:

- A clean brush and solvent degrease, then one coat of phosphoric acid based etch primer internally and externally followed by,

- One coat airless spray of coal tar pitch epoxy paint for a dry film thickness of 1 x 100 microns on the inner surface of poles.

- Two successive coat airless spray of coal tar pitch epoxy paint for a dry film thickness of 2 x 100 microns on the outer surface of poles.

Any tender not making provision for painting as above shall be rejected.

Any galvanized surface of the poles damaged after delivery and within the warranty period shall be scrapped back to a firm base and two full thickness and coats of Zinc rich primer applied to the damaged area and overlapping the sound galvanizing by 10(ten) mm. If, in the opinion of the Engineer, the damage to the galvanizing is extensive then that pole shall be removed from site and re-galvanized.

Marking of Pole:

The poles (each section) shall have an identification mark with indelible paint on the pole at a position approximately 3.5 meters from the butt end which is clearly and indelibly marked with:

- Date of manufacture.

- BPDB ownership & Name of Manufacturer.

- Length of pole in meters and its design working load, as defined in this specification.

For example, a 12-meter pole with a 450 daN working load shall be marked as 12m/450 daN.

The pole shall also be marked with a permanent horizontal line at a point up to plantation depth from the butt end. In case of sectional telescopic pole, all male sections shall be marked with permanent horizontal line at the respective overlapping length from the top.

Earthing Lugs, Base Plate and Pole Cap.

Each pole shall be provided with Earthing lugs at 300mm below ground level, Base plate and Pole cap of steel. The materials of the Base plate and Pole Cap shall be galvanized steel and minimum thickness of pole cap shall be 2.0 mm. The thickness of base plate shall be as like the thickness of bottom section and shall have proper fixing arrangements for easy fixing at site.

Pole Length, Shape and Design Loading

Included in the tender document schedules detailing the total number of each class of pole to be supplied under this contract and the required numbers that are to be delivered to the locations nominated in the schedule.

Pole Length and Shape

The standard overall length of poles manufactured under this contract shall be of 15 Meters/12 Meter/11 Meter/9 Meter telescopic steel pole.

The plantation depth of each pole shall be 1/6th of the overall length of that pole. The Bidder shall submit a detailed description of the methods of pole manufacture and detailed calculations for all aspects of design of the poles

Design Loading

The standard design working loads in the transverse direction shall be as follows:

| Total Length | Design load applied 300mm bellow pole top | Design vertical load |
| --- | --- | --- |
| 15 Meter Pole | 650 daN | 375 daN |
|  | 550 daN | 375 daN |
| 12 Meter Pole | 450 daN | 300 daN |
|  | 350 daN | 300 daN |
| 11 Meter Pole | 350 daN | 300 daN |
| 9 Meter Pole | 300 daN | 300 daN |
|  | 200 daN | 200 daN |

Each pole shall be designed on yield strength and factor of safety on yield strength shall be 2.0.

Wind Pressure

Following wind pressure have to be considered in addition to the design load by the manufacturer.

- Wind Pressure on Round surface	:	61kg/sq.m

- Wind Pressure on Flat surface	:           96 kg/sq.m

- Wind pressure on polygonal surface	:	87 kg/sq.m

Design of Poles

Each type of poles shall be design to have adequate strength under the ultimate design loads. The pole shall be designed with a factor of safety of 2.0 on yield strength.

The detailed combined stress calculations of each type of poles shall be submitted with the bid otherwise the bid shall be rejected.

Testing of Poles

The supplier/manufacturer shall make all arrangements and provide all facilities for pole testing detailed herein. Each class of pole shall be subjected to 2(two) types of tests:

a)  Type Test (Destruction Tests)

These shall be carried out to prove that each class of poles satisfies all the design requirements set out in these specifications.

Manufacture of poles to be supplied under this contract shall not commence until designs have been successfully type tested and the Engineer has certified the same.

b)  Proof Tests (Acceptance Tests)

These shall be carried out periodically to check the consistency of the standard of manufacture. Poles, which successfully pass proof tests, may form part of the contract for supply.

Testing Arrangement

Pole shall be tested in the horizontal position in a testing arrangement as per relevant standard. The testing arrangement shall be provided with sufficient support to ensure that bending moments developed by the self-weight of the pole are minimum. These supports shall be detailed to give on horizontal resistance to the applied loads. The accuracy of all loads and deflection measuring equipment shall be ±2%.

Observation of Testing

All tests shall be carried out by the supplier/manufacturer and the Engineer and/or the purchaser shall witness all aspects.

The supplier/manufacturer shall give the Purchaser a minimum of 15(fifteen) days’ notice before commencing any tests.

Cost of Testing

The costs of all the above testing shall be allowed for the tender price.  This shall include any additional testing instructed to be carried out by the Engineer/Purchaser to prove that a class of pole satisfied all design requirements.

Type Test

These shall be carried out before full scale manufacture of a class of pole commences; after any changes are made to the approved design of a class of pole; or at any time the Engineer/Purchaser considers necessary modification to confirm that any class of poles still satisfy the design requirements.

A sample considering of 3(three) poles from each class of poles, similar in all essential features or design and construction to those purchased, shall be subject to the Type test and must give evidence that the poles comply with the acceptance criteria of this specification.

The test arrangement facilities shall be available at manufacturer’s premises. The test shall be carried out in 2 stages.

- 1st Stage

The load shall be gradually and uniformly applied in increments of 20% of the Ultimate design load up to 120% of the design working load. At each increment of load the deflection of the pole tip shall be measured. The 120% loading shall be maintained for 5 (five) minutes. The load shall then be gradually reduced to zero and the amount of permanent deflection of the pole tip recorded.

- 2nd Stage

The test load shall gradually re-apply up to the working load and the deflection will be recorded. The load shall then be increased in 20% increments until failure occurs. At each load increment the load and deflection shall be recorded.

The following particulars shall be recorded for each test made:

- Manufacturer’s name and plant location.

- Pole classification and type.

- Dimension of the pole.

- Test report for offered pole materials.

- Date of manufacture.

- Tested date.

- Increments of load

- Deflection at each increment of load. (for both 1st and 2nd stage loading).

- Permanent deflection after removal of 1st stage loading.

- Load at failure.

- Nature of failure.

- Color photographs along the axis of the pole at design working and ultimate loads plus photographs of the failure zone on the pole.

The pole shall be considered acceptable if:

- Permanent deflection of the tip of the pole, after the 1st stage test loading is removed, does not exceed 3mm per meter of pole length for 9m and 11m poles and 4mm per meter of pole length for 12m and 15m poles.

- The average failure load of the 3(three) poles tested equals or exceeds the ultimate design load and the failure load of any single pole is not less than 0.90 times the ultimate design load

Proof Test:

These shall be carried out on poles selected at random by the Engineer/Purchaser at the following rate:

Lot Size			No. of Poles to be selected for Tests.

Up to 500 Nos.			5 Nos.

501 to 1000 Nos.			8 Nos.

1001 to 2000 Nos.			13 Nos.

2001 to 3000 Nos.			18 Nos.

3001 and above Nos.			20 Nos.

1st Stage Test

This test shall be carried out in the same manner as in the 1st stage test of the type test.

2nd stage Test.

The test load shall be gradually reapplied up to the working load and the deflection recorded. The load shall than be increased in 20% increments up to 200% working load.

The poles will be considered acceptable if the deflection at each load increment and the permanent deflection upon removal of load do not exceed by more than 15% the average of the acceptable tests of the corresponding values for 1st stage loading of the Type Tests the pole withstands at 200% working load without any type of failure.

Failure to Satisfy Acceptable Criteria.

In the event that a pole does not satisfy any of the above acceptable criteria for Proof Tests, then one more pole shall be tested for every one that does not meet these acceptance criteria. If any of these additional poles fail to satisfy the acceptance criteria then consultations shall be held with the Engineer and if so instructed the supplier/manufacturer shall modify the pole design or construction procedure to increase the strength of the pole.

In the event that any of the above acceptance criteria are not satisfied, then at the discretion of the Engineer, any poles manufactured in the same manner as those that have failed the acceptance test be rejected.

Quality Assurance.

The supplier/manufacturer shall submit with the bid an outline of the quality assurance practices that will be applied to all aspects of the pole manufacturing process.

Within one month or receipt of a letter of intent for supply of poles under this specification the supplier/manufacturer shall submit a detailed Quality Assurance Manual which conforms generally with the requirements of BS 5757: 1979 or equivalent standards. Approval to proceeds with this Quality Assurance Manual has been received an approved by the Engineer/Purchaser. Delays to the contract completion due to non-compliance with this specification requirement will be the supplier/manufacturer’s responsibility.

Major features of the Quality Assurance scheme practiced by the supplier/manufacturer and detailed in this Quality Assurance Manual shall be:

- The Supplier/Manufacturer has defined all staff responsibilities and the Quality Assurance System operating within the Organization for the purpose of ensuring adequate quality of the end product.

- The Supplier/Manufacturer has a senior staff with the authority to resolve matters of Quality to the satisfaction of the engineer.

- The Supplier/Manufacturer has adequate facilities under the control of properly trained staff to perform the quality control duties.

- All production operations and test function are properly documented and available to any relevant member of the Supplier/Manufacturer’s workforce.

- A detailed inspection test plan has been prepared for the whole manufacturing operation.

- Regular and systematic program of testing are carried out for all incoming raw materials.

- Regular calibration checks are carried out on all measuring equipment used in the manufacturing operations.

- That statistical analysis is carried out regularly on appropriate test results to confirm that all procedures are performing within the specified tolerance.

- That adequate procedures are planned for corrective action in the event that quality checks show that performance is not satisfactory.

- That all checking activities, test results etc. are recorded on appropriate standardization forms and these are verified, certified, recorded and filled is a systematic manner.

Claims for payment are to be accompanied by the quality assurance records for the same production period. If, in the opinion of the Engineer, the quality assurance records are incomplete or indicate that the poles produced during the production period may not conform with the specification then proof testing of the poles as per relevant standards unless otherwise specified shall be carried out.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

b)	Manufacturer's valid ISO 9001 Certificate.

3.0 Technical Specification of POLE FITTINGS

Standards

The equipment specified in this section shall conform to the latest edition of the appropriate IEC specifications and other recognized international standards. In particulars

BS EN ISO      	Hot dip galvanized coatings on fabricated iron and steel articles.

1461:1999

ASTM A90	        Standard test method for weight of coating on Zinc-coated (galvanized) iron or steel 		articles.

BS 4190:1967 	Isometric Hexagonal Bolts, Screws and Nuts.

BS 4360		Specification for weld able Structural Steel

BS 4870		Specification for approval testing of welding procedures.

BS 5757		Quality Assurance.

# If the Bidder offers other equivalent standards full details including copies in English Language of such standards shall be submitted with the offer.

General

This specification includes the design, manufacture, and testing of SPC/Steel Pole fittings.

Definitions and Abbreviations

The following definitions and abbreviations apply to the specification.

Definitions:

| i) | Failure | : | Inability of the pole fittings when under test to support further load or when deformation or buckling of the pole renders it unserviceable. |
| --- | --- | --- | --- |
| ii) | Longitudinal direction | : | The horizontal direction parallel to the run of the direction of the conductors. |
| iii) | Transverse direction | : | The horizontal direction at right angles to the run of direction of the conductors. |
| iv) | Ultimate Tensile Strength | : | The strength at which the pole fittings will not accept any further applied force or when deformation or buckling or the pole renders at unserviceable. |

Abbreviations

BS	: 	British Standard.

IEC	:	 International Electro-technical Commission

Mpa	: Mega Pascal = 1 N/sq. mm.

Material and Manufactures

Manufacturer’s test certificates for material strength shall be submitted. The test certificates shall show compliance with the relevant standard specifications in all respects. If the manufacturer’s test certificates are not available or if the Engineer/ Purchaser requires it then the supplier/ manufacturer is responsible for arranging all testing requested by the Engineer/ Purchaser.

The test information so obtained must be sufficient to satisfy the Engineer/ Purchaser that the item being tested conforms to the relevant standard specification.

Materials for Pole fittings

All materials shall be new and conform to the relevant standard referred in these specifications. All types of pole fittings and accessories shall be manufactured from material having minimum yield strength of 245 N/sq. mm as per BS 4360.

Corrosion Protection and Galvanizing

a) 	All pole fittings, including Nuts and Bolts, shall be hot-dip galvanized in accordance with BS EN ISO 1461:1999.

b) 	The zinc coating shall be smooth, clean and of uniform thickness and free from defects. All drilling, punching, cutting, shaping and welding of parts shall be completed and all burns shall be removed before the galvanizing process is applied.

c) 	Any galvanized surface of the pole fittings damaged after delivery and within the warranty period shall be scrapped back to a firm base and two full thickness and coats of Zinc rich primer applied to the damage to the galvanizing is extensive then that pole fittings shall be removed from site and re-galvanized.

Marking of Pole Fittings

Drawing number along with marking number (marking will be provided during sample approval) to be embossed or engraved directly on the all pole fittings. Dimensions/Diameter also marked if same drawing number’s fittings have different dimensions.

Design of Pole Fittings and Sample(s) Approval

The fittings shall be so designed that they fit with the specified poles. According to this, the samples manufactured as per the approved drawings shall be submitted to the Engineer for getting the concurrence on going to the mass production of the same. Before full scale manufacture is commenced, two samples of each type of fitting shall be prepared for examination and approval by the Engineer. Production items not meeting the same standard as the initial samples approved by the Engineer will be rejected.

Dimensional Tolerances

The permitted variation from stated dimension shall be as follows except mentioned otherwise.

Material sizes		:	±1 mm.

Thickness tolerance	:	-0%, +10%.

Manufacture

Pole fittings shall be manufactured to the details on the attached drawings and schedules and from the materials specified in this section.

All welding of the pole fittings shall be carried out in accordance with the procedures of an international standard approved by the Engineer and these procedures shall be tested in accordance with AWS standards at the manufacturer’s plant and before galvanization. All welding shall be continuous and shall be of a size and type capable of developing the full strength of the parent metal without permanent distortion in the finished fittings.

Quality Assurance

The manufacturer shall maintain the quality assurance practices that will be applied to all aspects of the pole fittings manufacturing process, which conforms generally to the requirements of BS 5757: 1979 or equivalent standards.

Drawings

All drawings of Pole Fittings are included. Poles may not have provision of holes for fixing the Pole Fittings. All sorts of Pole fittings shall be fixed by using clamps. Fixing arrangement of Pole Fittings with the pole shall be done according to the profile of the poles offered at different position of Poles. However the Supplier/ Manufacturer shall be responsible for ensuring overall fixing the Pole Fittings. The Supplier/ Manufacturer shall submit all the drawings of pole fittings to the Engineers for approval before manufacture.

4.0 Technical Specification of ACSR DOG CONDUCTOR

STANDARDS:

The conductor as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the conductor shall be in accordance with the BS-215 Part-2, IEC-209 & BDS-1037 or equivalent International standards.

Specifications:

This conductor shall be designed as per above standards for operation in overhead lines in air under local ambient conditions. The conductor shall be constructed from hard drawn Aluminium and Zinc Coated Steel wires where the centre wire or wires are of Zinc Coated Steel and the outer layer or layers are of Aluminium. The wires shall be smooth and free from all imperfections not consistent with good commercial practice. No joint of any kind shall be permitted in the Zinc Coated Steel wires.

In all constructions, the successive layers shall have opposite directions of lay, the outermost layer being right handed. The lay ratio of any Aluminium layer shall not be greater than the lay ratio of Aluminium layer immediately beneath it. The lay ratio of different layers shall be within the limit as per above standards.

The maximum acceptable length of conductor in a drum shall be as stated below and shall be supplied on standard non-returnable treated wooden drum, each drum having stenciled on each side: drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer's name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

Drum wound length of each drum may not vary of the total drum length as tolerance. However, the sum of total drum length shall be as per ordered quantity. Only one short length of conductor on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerances for the diameter and thickness are acceptable

| ACSR DOG |  |
| --- | --- |
| Code name | ACSR DOG |
| Installation | Overhead |
| Type | Stranded |
| Material | Hard drawn Aluminium steel reinforced |
| Density of hard drawn Aluminium wire at 20 °C | 2.703 Kg/dm3 |
| Density of Zinc Coated Steel wire at 20 °C | 7.80 Kg/dm3 |
| Overall diameter of the conductor | 14.15 mm |
| Nominal cross sectional area of the conductor | 118.47 sq. mm |
| Number/diameter of Aluminium Strand | 6/4.72 mm |
| Nominal Aluminium cross sectional area | 104.93 sq. mm |
| Number/diameter of Steel Strand | 7/1.57 mm |
| Nominal Steel cross sectional area | 13.56 sq. mm |
| Weight of conductor | 394 Kg/KM |
| Drum wound length | 1700 M |
| Maximum DC Resistance of Conductor at 20 °C | 0.2733 Ω/Km |
| Minimum breaking Load of Conductor | 3335 Kg |
| Lay ratio for Outermost Layer of Aluminium | 10-14 |
| Lay direction for Outermost Layer of Aluminium | Right hand |

FEATURES AND ACCESSORIES:

  - Conductors shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 95 mm diameter. The interior of the conductor drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Conductor drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate without undue deterioration.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

INFORMATION REQUIRED:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered conductor.

b)	Cross-sectional drawings of offered conductor.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)	Manufacturer's valid ISO 9001 Certificate.

e)	Type Test Reports for ACSR Dog Conductor from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

5.0 Technical Specification of AAC WASP (INSULATED) CONDUCTOR

STANDARDS:

The conductor as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the conductor shall be in accordance with the BS-215 Part-1, IEC-207, BDS-1036 & BS-6485 or equivalent International standards.

Specifications:

This conductor shall be designed as per above standards for operation in overhead lines in air under local ambient conditions. The conductor shall be constructed from hard drawn Aluminium wires. The wires shall be smooth and free from all imperfections not consistent with good commercial practice. There shall be no joints in any wire of a stranded conductor except hose made in the base wire before final drawing.

In all constructions, the successive layers shall have opposite directions of lay, the outermost layer being right handed. The lay ratio of any layer shall not be greater than the lay ratio of the layer immediately beneath it. The lay ratio of different layers shall be within the limit as per above standards.

A means of identifying the conductor size and BPDB ownership shall be inscribed throughout the  length of the conductor in a single line on the PVC pressure Insulation (AAC ANT, BPDB, manufacturer's name & year).  The letters shall be upright block characters embossed on the surface; they are being not more than 300 mm gap between each group. The Manufacturer's name with year of manufacture and progressive meter marking shall be provided throughout the length of the conductor.

The maximum acceptable length of conductor in a drum shall be as stated below and shall be supplied on standard non-returnable treated wooden drum, each drum having stenciled on each side: drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer's name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

The sum of total drum length shall be as per ordered quantity. Only one short length of conductor on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerances for the diameter and thickness are acceptable.

| AAC WASP (Insulated) Conductor |  |
| --- | --- |
| Code name | AAC WASP (Insulated) Conductor |
| Installation | Overhead |
| Type | Stranded |
| Material | Hard drawn Aluminium |
| Density of hard drawn Aluminium wire at 20 °C | 2.703 Kg/dm3 |
| Overall diameter | 15.57 mm |
| Diameter of bare conductor | 13.17 mm |
| Number/diameter of Aluminium | 7/4.39 mm |
| Nominal cross sectional area of conductors | 106.00 sq. mm |
| Insulation thickness (min.) | 0.8 mm |
| Color of Insulation | Black |
| Weight of bare conductor | 290 Kg/Km |
| Weight of insulated conductor | 389 Kg/Km |
| Drum wound length | 1300 M |
| Maximum DC Resistance of Conductor at 20 °C | 0.2702 Ω/Km |
| Minimum breaking Load of Conductor | 1632 Kg |
| Lay ratio of Outermost Layer | 10-14 |
| Lay direction of Outermost Layer | Right hand |

FEATURES AND ACCESSORIES:

  - Conductors shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 95 mm diameter. The interior of the conductor drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Conductor drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate with out undue deterioration.

  - The PVC covering shall complete with requirement of BS-6746 for type TI 1 compound.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

INFORMATION REQUIRED:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered conductor.

b)	Cross-sectional drawings of offered conductor.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)	Manufacturer's valid ISO 9001 Certificate.

e)	Type Test Reports for AAC WASP (Insulated) Conductor from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

6.0 Technical Specification of AAC ANT (INSULATED) CONDUCTOR

STANDARDS:

The conductor as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the conductor shall be in accordance with the BS-215 Part-1, IEC-207, BDS-1036 & BS-6485 or equivalent International standards.

Specifications:

This conductor shall be designed as per above standards for operation in overhead lines in air under local ambient conditions. The conductor shall be constructed from hard drawn Aluminium wires. The wires shall be smooth and free from all imperfections not consistent with good commercial practice. There shall be no joints in any wire of a stranded conductor except hose made in the base wire before final drawing.

In all constructions, the successive layers shall have opposite directions of lay, the outermost layer being right handed. The lay ratio of any layer shall not be greater than the lay ratio of the layer immediately beneath it. The lay ratio of different layers shall be within the limit as per above standards.

A means of identifying the conductor size and BPDB ownership shall be inscribed throughout the the length of the conductor in a single line on the PVC pressure Insulation (AAC ANT, BPDB, manufacturer's name & year).  The letters shall be upright block characters embossed on the surface; they are being not more than 300 mm gap between each group. The Manufacturer's name with year of manufacture and progressive meter marking shall be provided throughout the length of the conductor.

The maximum acceptable length of conductor in a drum shall be as stated below and shall be supplied on standard non-returnable treated wooden drum, each drum having stenciled on each side: drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer's name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

The sum of total drum length shall be as per ordered quantity. Only one short length of conductor on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerances for the diameter and thickness are acceptable.

| AAC ANT (Insulated) Conductor |  |
| --- | --- |
| Code name | AAC ANT (Insulated) |
| Installation | Overhead |
| Type | Stranded |
| Material | Hard drawn Aluminium |
| Density of hard drawn Aluminium wire at 20 °C | 2.703 Kg/dm3 |
| Overall diameter | 11.30 mm |
| Diameter of bare conductor | 9.30 mm |
| Number/diameter of Aluminium | 7/3.10 mm |
| Nominal cross sectional area of conductors | 52.84 sq. mm |
| Insulation thickness (min.) | 0.8 mm |
| Colour of Insulation | Black |
| Weight of bare conductor | 145 Kg/Km |
| Weight of insulated conductor | 200Kg/Km |
| Drum wound length | 2200 M |
| Maximum DC Resistance of Conductor at 20 °C | 0.5419 Ω/Km |
| Minimum breaking Load of Conductor | 845 Kg |
| Lay ratio of Outermost Layer | 10-14 |
| Lay direction of Outermost Layer | Right hand |

FEATURES AND ACCESSORIES:

  - Conductors shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 95 mm diameter. The interior of the conductor drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Conductor drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate without undue deterioration.

  - The PVC covering shall complete with requirement of BS-6746 for type TI 1 compound.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

INFORMATION REQUIRED:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered conductor.

b)	Cross-sectional drawings of offered conductor.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)	Manufacturer's valid ISO 9001 Certificate.

e)	Type Test Reports for AAC ANT (Insulated) Conductor from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

7.0 Technical Specification of GUY/EARTH WIRE

STANDARDS:

The wire as specified in this Section shall be conforming to the latest edition of the following standards for operation in overhead lines or in stay in air under local ambient conditions. Design, Manufacture, Testing and Performance of the G u y / E a r t h Wire shall be in accordance with the BS-183, Grade 1150, ASTM B498-74, Class-A or equivalent International standards.

SPECIFICATIONS:

This wire shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

The maximum acceptable length of wire in a drum shall be as stated below and shall be supplied on standard non-returnable treated wooden drum, each drum having stenciled on each side, drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

Drum wound length of each drum may vary up to ± 5% of the total drum length as tolerance. However, the sum of total drum length shall be as per ordered quantity. Only one short length of wire on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerance for the diameter is acceptable.

| Guy Wire |  |
| --- | --- |
| Code name | Guy Wire/Earth Wire |
| Installation | Overhead/Stay |
| Type | Stranded, Solid and Bare |
| Material | High Strength Steel |
| Overall diameter | 9.5 mm |
| Number/diameter of each strand | 7/3.15 mm |
| Nominal cross sectional area | 54.53 sq. mm |
| Weight of wire | 430 Kg/Km |
| Drum wound length | 1500 M |
| Ultimate Tensile Strength | 62.75 KN |
| Galvanisation | As per ASTM B498-74, Class-A |
| Lay ratio | 13-18 |
| Lay direction | Right hand |

Features And Accessories:

  - Wire shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 95 mm diameter. The interior of the wire drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Wire drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate with out undue deterioration.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

INFORMATION REQUIRED:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered Guy Wire/Earth

Wire.

b)	Cross-sectional drawings of offered Guy Wire/Earth Wire.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)	 Manufacturer's valid ISO 9001 Certificate.

e)	Type Test Reports for Guy / Earth  Wire (having overall diameter of 9.50 mm) from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

8.0 Technical Specification of 11KV PIN INSULATOR WITH PIN

STANDARDS:

These 11kV PIN Insulator with Pin specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance shall be in accordance with latest revisions of BS, IEC standards as listed below or other equivalent internationally acceptable Standards:

BS-137     			: 	Method of test & requirements.

BS-916     			: 	Bolts, Screws & Nuts.

BS-3288   			: 	Performance & general requirements and Dimensions.

IEC-383   			: 	Insulator Tests.

IEC-575   			: 	Insulator Tests

IEC-437   			: 	Radio Interference Tests.

BS 4360 or ASTM A-36		:	Steel Quality

BS 729 part-1 or ASTM A-153	:	Galvanization

Specifications:

These 11 kV Pin Insulators with Pin shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

| 1.1 | Installation | : | Overhead line, Steel cross-arm mounting. |
| --- | --- | --- | --- |
| 1.2 | Nominal System Voltage, kV | : | 11 (line to line). |
| 1.3 | Type of System | : | Three phase, 50 Hz, Three Wire, effectively earthed. |
| 1.4 | Highest System Voltage, kV | : | 12 |
| 1.5 | Atmospheric Condition | : | Moderately polluted. |
| 1.6 | Altitude, meter | : | 0-300 above sea level. |
| 1.7 | Maximum Ambient Temperature | : | 48ºC |
| 1.8 | Insulator Material | : | The Insulator shall be made of good commercial grade wet process porcelain. The porcelain shall be sound, thoroughly vitrified and free from defects and blemishes which might adversely affect the life of the Insulator. The exposed parts of the porcelain shall be smoothly glazed and shall be brown in color unless otherwise specified. |
| 1.9 | Type of Insulator | : | Pin, Radio Freed. |
| 1.10 | Insulator Head & Neck | : | The Insulator Shall have head and neck suitable for fastening the tie wire or preformed fittings. Conductor sizes up to 170 mm2 ACSR including line guards. |
| 1.11 | Markings | : | Each Insulator shall be marked with the name of Trade Mark of the manufacturer, the type of Insulator and the year of manufacture. These markings shall be legible and indelible. |
| 1.12 | Creepage Distance minimum, mm | : | 275 |
| 2.0 2.1 2.2 2.3 | WITHSTAND VOLTAGE,MINIMUM Power Frequency, dry (one minute), kV Power Frequency, wet (one minute),kV Impulse 1.2x50 micro-sec wave, kV | : : : | 65 45 95 |
| 3.0 | FLASHOVER VOLTAGE,MINIMUM |  |  |
| 3.1 3.2 3.3 3.4 | Power Frequency, dry, kV Power Frequency, wet, kV 50% Impulse 1.2x50 micro-sec wave, positive, kV 50% Impulse 1.2x50 micro-sec wave, negative, kV | : : : : | 75 50 115 150 |
| 4.0 | POWER FREQUENCY PUNCTURE VOLTAGE MINIMUM, kV | : | 150 |
| 5.0 | RADIO-INFLUENCE VOLTAGE DATA |  |  |
| 5.1 | Power Frequency Test Voltage RMS to Ground, kV | : | 15 |
| 5.2 | Maximum RIV at 1000 KC Micro-volt | : | 100 |
| 6.0 | MECHANICAL FAILING LOAD, MINIMUM, kN | : | 10.7 |
| 7.0 | CONSTRUCTION OF PIN |  |  |
| 7.1 | Type of Pin | : | Line type, tapered style with threaded shank made of forged steel galvanized, complete with nut, lock nut and thick washers for use in steel cross-arm. |
| 7.2 | Pin Steel Head | : | Large head shall be suitable for screwing into thimble fixed in Insulator pin hole. Minimum threaded length shall be 44.4 mm and diameter 18.3 mm. |
| 7.3 | Pin Stalk Length | : | 230 mm measured above seating face of the collar. |
| 7.4 | Pin Shank Length | : | 50 mm (for short shank) and 140 (for long shank) measured below seating face of the collar. Threaded length 45 mm (for short shank) and 70 mm (for long shank) and diameter 22 mm. |
| 7.5 | Minimum Failing Load of Pin, kN | : | 10.7 |
| 7.6 | Steel Quality | : | Pin, Nuts & Washers shall be made of mild steel as per BS 4360 or ASTM A-36. Pin shall be forged steel galvanized. |
| 7.8 | Galvanization | : | Pin, Nuts & Washers shall be hot dip galvanized as per BS 729 part-1 or ASTM A-153. |
| 7.9 | Minimum neck diameter (mm) | : | 73 |
| 7.10 | Minimum Diameter of insulator (mm) | : | 150 |
| 7.11 | Minimum Height of Insulator (mm) | : | 150 |
| 7.12 | Minimum Grove diameter (mm) | : | 22 |
| 8.0 | Each Insulator shall be supplied with Pin The ultimate mechanical strength of the Pin Insulator assembly shall be not less than the above cantilever strength. |  |  |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered 11 KV Pin insulator with pin.

b)	Detail dimensional drawings of offered 11 KV Pin insulator with Pin.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)      Manufacturer's valid ISO 9001 Certificate.

e)  Type Test Reports for offered Pin Insulator from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

9.0 Technical Specification of 11KV DISC INSULATOR WITH FITTINGS

STANDARDS:

These 11 kV Disc Insulator with Fittings specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance shall be in accordance with latest revisions of BS, IEC standards as listed below or other equivalent internationally acceptable Standards:

IEC-120	:   	Ball & Socket Coupling.

IEC-305             :   	Characteristics of String Insulator Unit.

IEC-383	:   	Insulator Tests.

IEC-437	:   	Radio Interference Tests.

IEC-506	:   	Switching Impulse Tests.

IEC-575             :   	Thermal Mechanical Performance Tests.

BS-137              :   	Method of test & requirements.

BS-916              :   	Bolts, Screws & Nuts.

Specifications:

These 11 kV Disc Insulators shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

| 1. | Installation | : | Overhead line for suspension or termination. |
| --- | --- | --- | --- |
| 2. | Nominal System Voltage, kV | : | 11 (line to line). |
| 3. | Type of System | : | Three phase, 50 Hz, Three Wire, effectively earthed. |
| 4. | Highest System Voltage, kV | : | 12 (three phase). |
| 5. | Atmospheric Condition | : | Moderately polluted. |
| 6. | Altitude, meter | : | 0-300 above sea level. |
| 7. | Maximum Ambient Temperature, ºC | : | 45. |
| 8. | Insulator Material | : | The Insulator shall be made of good commercial grade wet process porcelain. The porcelain shall be sound, thoroughly vitrified and free from defects and blemishes that might adversely affect the life of the Insulator. The exposed parts of the porcelain shall be smoothly glazed and shall be brown in color unless otherwise specified. |
| 9. | Type of Insulator | : | Ball & Socket type Disc, security clip made of Stainless Steel or Phosphor Bronze. |
| 10. | Markings | : | Each Insulator shall be marked with the name of Trade Mark of the manufacturer, the type of Insulator and the year of manufacture. These markings shall be legible and indelible. |
| 11. | Maximum Nominal Diameter of Insulator, mm | : | 255 |
| 12. | Nominal Spacing, mm | : | 146 |
| 13. | Minimum Nominal Creepage Distance, mm | : | 292 |
| 14. | Coupling Size, mm | : | 16 |
| 15. 15.1 15.2 15.3 | WITHSTAND VOLTAGE, MINIMUM Power Frequency, dry (one minute), kV Power Frequency, wet (one minute), kV Impulse 1.2x50 micro-sec wave, kV | : : : | 70 40 110 |
| 16. 16.1 16.2 16.3 16.4 | FLASHOVER VOLTAGE, MINIMUM Power Frequency, dry, kV Power Frequency, wet, kV 50% Impulse 1.2x50 micro-sec wave, positive, kV 50% Impulse 1.2x50 micro-sec wave, negative, kV | : : : : | 78 45 120 125 |
| 17. | POWER FREQUENCY PUNCTURE VOLTAGE MINIMUM, kV | : | 110 |
| 18. 18.1 18.2 | RADIO-INFLUENCE VOLTAGE DATA MINIMUM: Power Frequency Test Voltage, RMS to Ground, kV Maximum RIV at 1000 KC Micro-volt | : : | 10 50 |
| 19. | MECHANICAL FAILING LOAD MINIMUM, kN | : | 70 |

Specification of 11 kV Strain Insulator String Set:

| 11 kV Strain Insulator String Set consisting of the following component parts for each set. Design, Manufacture, Testing and Performance shall be in accordance with latest revisions of BS-3288 or other equivalent internationally acceptable Standards. |  |  |  |
| --- | --- | --- | --- |
| 1. | Anchor Shackle | : | Made of forged steel galvanized complete with cotter bolt and Pin, UTS-4500 Kg, Galvanization as per BS-729 part 1 or ASTM A-153. |
| 2. | Ball Eye | : | Oval eye type, made of forged steel galvanized, UTS-4500 Kg, Galvanization as per BS- 729 part 1 or ASTM A-153. |
| 3. | Socket Eye | : | Made of malleable iron galvanized complete with cotter bolt and Pin, UTS-4500 Kg, Galvanization as per BS- 729 part 1 or ASTM A-153. |
| 4. | Strain Clamp | : | Bolted type, Made of malleable iron galvanized or Alluminium Alloy, suitable for accommodating ACSR DOG of overall diameter 14.15 mm, complete with bolts, nuts, washers, Alluminium Alloy liner etc., UTS-4500 Kg, Galvanization as per BS- 729 part 1 or ASTM A-153 in case of malleable iron or other ferrous metal. |
| 5. | Disc Insulator | : | 2 (Two) Nos. are required for each set. |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered Disc insulator.

b)	Detail dimensional drawings of offered Disc insulators and Disc Fittings.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)    Manufacturer's valid ISO 9001 Certificate.

e)  Type Test Reports for offered Disc Insulator from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified);

10.0 Technical Specification of 0.4KV SHACKLE INSULATOR

STANDARDS:

These LT Shackle Insulators specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance shall be in accordance to latest revisions of BS, IEC standards as listed below or other equivalent internationally acceptable Standards:

ANSI C 29.1:

BS-137     : 	Method of test & requirements.

BS-3288   : 	Performance & general requirements and Dimensions.

IEC-383    : 	Insulator Tests.

IEC-575    : 	Insulator Tests

IEC-437    : 	Radio Interference Tests.

Specifications:

These LT Shackle Insulators shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

| 1. | Installation | : | Overhead line Pole vertical arrangement. |
| --- | --- | --- | --- |
| 2. | Nominal System Voltage, kV | : | - (line to line). |
| 3. | Type of System | : | Three phase, Four Wire, Effectively earthed neutral. |
| 4. | System Frequency, Hz | : | 50 |
| 5. | Atmospheric Condition | : | Moderately polluted. |
| 6. | Altitude, meter | : | 0-300 above sea level. |
| 7. | Maximum Ambient Temperature | : | 45º C |
| 8. | Insulator Material | : | The Insulator shall be made of good commercial grade wet process porcelain. The porcelain shall be sound, thoroughly vitrified and free from defects and blemishes that might adversely affect the life of the Insulator. |
| 9. | Shape | : | Shall be generally cylindrical form, having an axial hole and circumferential groove for fixing conductor with the tie wire. |
| 10. | Finish | : | The exposed parts of the porcelain shall be smoothly glazed and shall be brown/white in colour and shall bear a symbol identifying the manufacturer and the voltage class. |
| 11. | Markings | : | Each Insulator shall be marked with the name of Trade Mark of the manufacturer, the type of Insulator and the year of manufacture. These markings shall be legible and indelible. |
| 12. | Height maximum, mm | : | 76 |
| 13. | Diameter Maximum, mm | : | 89 |
| 14. | Groove Diameter, mm | : | 19 |
| 15. | Insulator Hole Diameter, mm | : | 17.5 |
| 16. | Leakage Distance, mm | : | 64 |
| 18. | Power Frequency Puncture Voltage Minimum, Kv | : | 70 |
| 19. | Transverse Strength Minimum, Kg | : | 1140 |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered LT Shackle Insulator.

b)	Detail dimensional drawings of offered LT Shackle Insulator.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)     Manufacturer's valid ISO 9001 Certificate.

e)  Type Test Reports for offered LT Shackle Insulator from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

11.0 Technical Specification of 11kV Guy Insulator

STANDARDS:

These 11 kV Guy Insulators specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance shall be in accordance with latest revisions of BS, IEC, ANSI standards as listed below or other equivalent internationally acceptable Standards:

ANSI C 29.1

ANSI C 29.4

BS-137    : 	Method of test & requirements.

BS-3288  : 	Performance & general requirements and Dimensions.

IEC-383   : 	Insulator Tests.

IEC-575   : 	Insulator Tests

IEC-437   : 	Radio Interference Tests.

Specifications:

These 11 kV Guy Insulators shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

| 1. | Installation | : | Overhead lines Pole stay tension. |
| --- | --- | --- | --- |
| 2. | Nominal System Voltage, kV | : | 11 (Line to line). |
| 3. | Type of System | : | Three phases, three Wires, effectively earthed. |
| 4. | System Frequency, Hz | : | 5 |
| 5. | Atmospheric Condition | : | Moderately polluted. |
| 6. | Altitude, meter | : | 0-300 above sea level. |
| 7. | Maximum Ambient Temperature | : | 45º C |
| 8. | Insulator Material | : | The Insulator shall be made of good commercial grade wet process porcelain. The porcelain shall be sound, thoroughly vitrified and free from defects and blemishes that might adversely affect the life of the Insulator. |
| 9. | Shape | : | Shall be generally cylindrical form, having two diametrical holes for fixing stay wire. |
| 10. | Finish | : | The exposed parts of the porcelain shall be smoothly glazed and shall be brown in color and shall bear a symbol identifying the manufacturer and the voltage class. |
| 11. | Markings | : | Each Insulator shall be marked with the name of Trade Mark of the manufacturer, the type of Insulator and the year of manufacture. These markings shall be legible and indelible. |
| 12. | Length minimum, mm | : | 108 |
| 13. | Largest Diameter Minimum, mm | : | 73 |
| 14. | Insulator Hole Diameter, mm | : | 22 |
| 15. | Leakage Distance, mm | : | 48 |
| 16. 16.1 16.2 | FLASHOVER VOLTAGE, MINIMUM Power Frequency, dry, kV Power Frequency, wet, kV | : : | 30 15 |
| 17. | TENSILE STRENGTH MINIMUM, KN | : | 53.44 |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered 11 kV Guy insulator.

b)	Detail dimensional drawings of offered 11 kV Guy insulator.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)     Manufacturer's valid ISO 9001 Certificate.

e)  Type Test Reports for offered 11 kV Guy Insulator from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

12.0 Technical Specification of 0.4kV Guy Insulator

STANDARDS:

These 0.4kV Guy Insulators specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance shall be in accordance with latest revisions of BS, IEC, ANSI standards as listed below or other equivalent internationally acceptable Standards:

ANSI C 29.1

ANSI C 29.4

BS-137  : 	Method of test & requirements.

BS-3288 : 	Performance & general requirements and Dimensions.

IEC-383  : 	Insulator Tests.

IEC-575  : 	Insulator Tests

IEC-437  : 	Radio Interference Tests.

Specifications:

These 0.4kV Guy Insulators shall be designed as per above standards for operation in overhead lines in air under local ambient conditions.

| 1. | Installation | : | Overhead lines Pole stay tension. |
| --- | --- | --- | --- |
| 2. | Nominal System Voltage, kV | : | 0.415 (Line to line). |
| 3. | Type of System | : | Three phases, four Wires, Effectively earthed neutral. |
| 4. | System Frequency, Hz | : | 50 |
| 5. | Atmospheric Condition | : | Moderately polluted. |
| 6. | Altitude, meter | : | 0-300 above sea level. |
| 7. | Maximum Ambient Temperature | : | 45º C |
| 8. | Insulator Material | : | The Insulator shall be made of good commercial grade wet process porcelain. The porcelain shall be sound, thoroughly vitrified and free from defects and blemishes that might adversely affect the life of the Insulator. |
| 9. | Shape | : | Shall be generally cylindrical form, having two diametrical holes for fixing stay wire. |
| 10. | Finish | : | The exposed parts of the porcelain shall be smoothly glazed and shall be brown in color and shall bear a symbol identifying the manufacturer and the voltage class. |
| 11. | Markings | : | Each Insulator shall be marked with the name of Trade Mark of the manufacturer, the type of Insulator and the year of manufacture. These markings shall be legible and indelible. |
| 12. | Length minimum, mm | : | 89 |
| 13. | Largest Diameter Minimum, mm | : | 64 |
| 14. | Insulator Hole Diameter, mm | : | 16 |
| 15. | Leakage Distance, mm | : | 41 |
| 16. 16.1 16.2 | FLASHOVER VOLTAGE, MINIMUM Power Frequency, dry, kV Power Frequency, wet, kV | : : | 25 12 |
| 17. | TENSILE STRENGTH MINIMUM, KN | : | 44.60 |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered 0.4kV Guy insulator.

b)	Detail dimensional drawings of offered 0.4kV Guy insulator.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)    Manufacturer's valid ISO 9001 Certificate.

e)  Type Test Reports for offered 0.4 KV Guy Insulator from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

13.0 Technical Specifications/requirements of Mid Span Joint

Standards:

The Mid Span Joints as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the Mid Span Joints shall be in accordance with the BS-3288 Part-1 & BS-4579 Part 3 or equivalent International standards.

Specifications:

Compression type Mid Span Joints shall be used in jointing the overhead lines constructed with AAC & ACSR. Comprising of inner steel sleeve for ACSR, these inner steel sleeves along with outer Aluminium alloy sleeves must be constructed tube type to accommodate the conductor on which they are fitted.

Minimum Lengths/dia of Mid Spain Joints are as follows:

|  | Aluminium Sleeve |  |  | Steel Sleeve |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | L | OD | ID | L | od | id |
| ACSR GROSBEAK | 690 mm | 43 mm | 27 mm | 210 mm | 18 mm | 9.5 mm |
| ACSR MERLIN | 450 mm | 33 mm | 19 mm | 120 mm | 12 mm | 4 mm |
| ACSR DOG | 320 mm | 30 mm | 16 mm | 115 mm | 12 mm | 5 mm |
| AAC WASP | 270 mm | 22 mm | 15 mm | Nil | Nil | Nil |
| AAC ANT | 200 mm | 18 mm | 12 mm | Nil | Nil | Nil |

These mid span joints shall be designed to develop 95% of the full rated breaking strength and to withstand the rated current carrying capacity of the conductor on which they are fitted.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)  	Manufacturer’s Printed Catalogue describing specification and technical data for offered Accessories.

b)	Dimensional drawing of offered Accessories.

c)	Detail description of testing facilities at manufacturer's plant.

d)	Test Reports for offered Mid Span Joints from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

14.0 Technical Specifications/Requirements of H-Type Connector

STANDARDS:

The H-Type Connectors as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the H-Type Connector shall be in accordance with the BS-3288 Part-1 & BS-4579 Part 3 or equivalent International standards.

Specifications:

The H-Type Connectors will be used for connecting the ACSR Conductors to ACSR Conductors, AAC Conductors to AAC Conductors and Copper Conductors to AAC conductors. These should be Uni-metal or Bi-metal type according to the contractions and applications of such connectors.

These should be made from high conductivity Aluminium and pre-filled with oxide inhabiting compound. The design of the compression type connectors should be such that galvanic corrosion is minimised. Conductor rough & tooling shall be clearly joined on the connectors.

The connector must have at least the same conductance as the conductor for which it is intended to be used and shall carry the full continuous current rating of the conductor size they are designed for.

The original quality of contacts shall be maintained through out the service life of the connectors. Glow discharge and radio interference must be reduced to a minimum level. All compression type connectors shall be suitable for installation, using either manual or hydraulic compression tools.

The size of the connectors for different Conductors is as follows:

|  | Grove A |  | Grove B |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Max (mm2) | Min (mm2) | Max (mm2) | Min (mm2) | Length in mm |
| ACSR GROSBEAK / ACSR GROSBEAK | 385 | 370 | 385 | 370 | 125.00 |
| ACSR MERLIN / ACSR MERLIN | 185 | 150 | 185 | 150 | 112.00 |
| ACSR DOG / ACSR DOG | 120 | 95 | 120 | 95 | 63.00 |
| AAC WASP / AAC WASP | 120 | 95 | 120 | 95 | 63.00 |
| AAC ANT / AAC ANT | 70 | 50 | 70 | 50 | 47.00 |
| AAC WASP / Service Bail | 120 | 95 | 35 | 16 | 63.00 |
| AAC ANT / Service Bail | 70 | 50 | 35 | 16 | 47.00 |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)  	Manufacturer’s Printed Catalogue describing specification and technical data for offered Accessories.

b)	Dimensional drawing of offered Accessories.

c)	Detail description of testing facilities at manufacturer's plant.

d)	Test Reports for offered H-Type Connectors from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

15.0 Technical Specifications/Requirements of PG Clamp

Standards:

The PG Clamps as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the PG Clamp shall be in accordance with the BS-3288 Part-1 & BS-4579 Part 3 or equivalent International standards.

Specifications:

The PG Clamps will be used for connecting the ACSR Conductors to ACSR Conductors and AAC Conductors to AAC Conductors. Parallel Groove Clamp, a non tension bolted type connector, shall be made of Aluminium Alloy, massively designed body. The bolts are made of Galvanised Steel. For the insulated conductors, 0.80 mm thick PVC insulation cover is to be provided with full length clamp.

The clamps must have at least the same conductance as the conductor for which it is intended to be used and shall carry the full continuous current rating of the conductor size they are designed for.

The original quality of contacts shall be maintained through out the service life of the clamps. Glow discharge and radio interference must be reduced to a minimum level.

The size of the connectors for different Clamps is as follows:

|  | Conductor Size (sq. mm) | Conductor Diameter (mm) | Dimension |  | No. of Bolt |
| --- | --- | --- | --- | --- | --- |
|  |  |  | L (mm) | W (mm) |  |
| ACSR GROSBEAK, either side | 375 | 25.15 | 125 | 50 | 3 |
| ACSR MERLIN, either side | 170 | 17.35 | 110 | 45 | 3 |
| ACSR DOG, either side | 100 | 14.15 | 95 | 30 | 2 |
| ACSR RABBIT, either side | 50 | 10.05 | 80 | 22 | 2 |
| AAC WASP, either side | 100 | 13.17 | 95 | 30 | 2 |
| AAC ANT, either side | 50 | 9.30 | 80 | 22 | 2 |

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)  	Manufacturer’s Printed Catalogue describing specification and technical data for offered Accessories.

b)	Dimensional drawing of offered Accessories.

c)	Detail description of testing facilities at manufacturer's plant.

d)	Test Reports for offered PG Clamps from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

16.0 Technical Specifications/Requirements of Preformed Termination

Standards:

The Preformed Termination as specified in this Section shall be conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the Preformed Termination shall be in accordance with the BS-3288 Part-1 & BS-4579 Part 3 or equivalent International standards.

Specifications:

Preformed Terminations shall be fabricated from Aluminium coated steel as per ASTM  A 474  and have a gritted, corrosion preventive gripping substance applied uniformly to the inside of the grip. This gripping substance shall be adhered to the grip in such a manner that it will sustain at least 3 (three) applications. Hand application of the glue and grit will not be acceptable. The glue and grit must be applied using an automatic machine. Fused Aluminium Oxide shall be used as grit (Grit size is # 80) and Synthetic Vinyl Resin shall be used as glue.

| Nominal Size (mm2) | Material to be terminated | Length mm | Centre Color Code |
| --- | --- | --- | --- |
| 100 | ACSR Dog Bare Conductor | 900 | Black |
| 50 | ACSR Rabbit Bare Conductor | 800 | Yellow |
| 100 | AAC WASP, PVC Insulated Conductor. | 800 | Yellow |
| 50 | AAC ANT, PVC Insulated Conductor. | 700 | White |
| 25 | AAC GNAT, PVC Insulated Conductor. | 600 | Red |
| 50 | Galvanized Steel Guy Wire. | 900 | Black |

Preformed Terminations shall have a minimum holding strength (before slippage occurs) equal to 95% of the UTS of the designated ACSR, AAC & GS Guy Wire and shall be complied with the relevant standard for design, performance, manufacture and testing.

All surfaces of preformed strain relief grips shall be free from blemishes or irregularities. The steel wires shall be Aluminium coated with right hand pitch. The grip shall be tagged with the manufacturer’s identification tape containing conductor nominal sizes in a manner and location that shall not impair its function. In addition, the grip shall also have the color code identification clearly printed at the installation crossover starting point of the grip.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)  	Manufacturer’s Printed Catalogue describing specification and technical data for offered Accessories.

b)	Dimensional drawing of offered Accessories.

c)	Detail description of testing facilities at manufacturer's plant.

d)	Test Reports for offered Preformed Terminations from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

17.0 Technical Specifications/Requirements of Preformed Armor Rod

Standards:

The Preformed Armor Rod as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the Preformed Armor Rod shall be in accordance with the BS-3288 Part-1, BS-4579 Part 3, ASTM B 211 Heat Treated Alloy 6061 or equivalent International standards.

Specifications:

Preformed armor rod shall be made of Aluminium alloy, right hand pitch that conforms to the requirements of ASTM B 211 Heat Treated Alloy 6061 or equivalent and shall be supplied for suitable fixing of the following conductors:

| Nominal Size (mm2) |  | Material to be terminated |
| --- | --- | --- |
| 370 170 |  | ACSR GROSBEAK, Bare Conductor ACSR MERLIN, Bare Conductor. |
| 100 |  | ACSR DOG, Bare Conductor. |
| 50 |  | ACSR RABBIT, Bare Conductor. |

Slipping strength of the above Armor rod shall be 25% of the Conductor UTS and shall complied with the relevant standard for design, performance, manufacture and testing.

# Preformed Armor rod shall be bundled into specific numbers of rods (set) and each set shall be provided with a tag indicating the size of the conductor with which the rods are to be used.

| Item | Nominal Conductor Size mm2 | Conductor Diameter, mm | Rod Length, mm | Rod Diameter, mm | No. of Rods per set | Centre Colour Code |
| --- | --- | --- | --- | --- | --- | --- |
| ACSR GROSBEAK | 370 | 25.15 | 2340 | 7.87 | 11 | Green |
| ACSR MERLIN | 170 | 17.35 | 1730 | 5.18 | 12 | Red |
| ACSR DOG | 100 | 14.15 | 1520 | 4.62 | 11 | Black |
| ACSR RABBIT | 50 | 10.05 | 1320 | 4.24 | 9 | Yellow |

# Preformed Armor rod shall have smooth surfaces and rounded ends and shall feed the conductor snugly. At the center starting cross over mark of each size Preformed Armor rod, there shall be a color code applied as indicated in the table.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)  	Manufacturer’s Printed Catalogue describing specification and technical data for offered Accessories.

b)	Dimensional drawing of offered Accessories.

c)	Detail description of testing facilities at manufacturer's plant.

d)	Test Reports for offered Preformed Armor rod from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

17.0 Technical Specifications/Requirements of Aluminium Binding Wire (Bare)

Standards:

The Aluminium Binding Wire (Bare) as specified in this Section shall conform to the latest edition of the following standards for operation in overhead lines in air under local ambient conditions. Design, Manufacture, Testing and Performance of the wire shall be in accordance with the BS-3288 Part-1 & BS-4579 Part 3 or equivalent International standards.

Specifications:

Aluminium Binding Wire (Bare) is required for binding of ACSR DOG with 11kV Insulators in HT lines. The Aluminium Binding Wire shall be solid and bare.

| Aluminium Binding Wire (Bare) |  |
| --- | --- |
| Code name | Aluminium Binding Wire (Bare) |
| Installation | Overhead lines (Routine Tie Wire) |
| Type | Solid and bare |
| Material | Aluminium Alloy (annealed & soft). |
| Strand | Single |
| Diameter of Wire | 4.15 mm |
| Cross Sectional Area of Wire | 13.5 mm2 |
| Breaking Strength | 700-1000 Kg/cm2 |
| Length of wire per reel | 1500 M |

Wire length of each reel may vary up to ± 5% of the total reel length as tolerance. Only one short length of wire on a reel is considered for acceptance, if necessary. No negative tolerances for the diameter are acceptable.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Cross-sectional drawings of offered wire.

b)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

c)	Test Reports for offered Aluminium Binding Wire (Bare) from an independent testing Laboratory/ Institute as per relevant Standards (unless otherwise specified).

## 18.0 Technical Specifications/Requirements of 11/0.415KV, 250KVA; 100KVA & 50KVA 3-Phase Distribution Transformer

## Standards

The equipment specified in this Section shall conform to the latest edition of the appropriate IEC specifications and other recognized international standard. In particular:

| IEC | 60076 | Power Transformers. |
| --- | --- | --- |
| IEC | 60137 | Bushings for alternating voltages above 1 kV. |
| IEC | 60156 | Method of determination of electrical strength of insulating oils. |
| IEC | 60296 | Specification for unused mineral insulating oils for transformers and switchgear. |
| IEC | 60551 | Measurement of transformer and reactor sound levels. |
| IEC | 60616 | Terminal and tapping markings for power transformers. |
| IEC | 60722 | Guide to lightning and switching impulse testing of power transformers. |
| IEC | 60529-3 | Protective coating of iron and steel structures against corrosion. |
| ASTM A90/ BS EN ISO 1461:1999 |  | Galvanization |
| IEC 60296 & BS 148 |  | Transformer Oil |

## Specifications

| 1. | Installation | Outdoor, Tropical, High Rainfall & Humidity |  |
| --- | --- | --- | --- |
| 2. | Type | Stack Core or Wound Core |  |
| 3. | Coolant | Mineral oil |  |
| 4. | Method of Cooling | ONAN |  |
| 5. | Phases | 3 (Three) |  |
| 6. | Frequency | 50 Hz. |  |
| 7. | Winding | Two windings of high conductivity copper |  |
| 8. | KVA Rating | 250 KVA, 100KVA & 50KVA |  |
| 9. | Rated Voltage at no-load | 11/0.415 kV |  |
| 10. | Vector Group | Dyn11 |  |
| 11. | Percentage Impedance at 750C, % | 4 % |  |
| 12. | No Load Loss | Maximum 520, 245 & 155 Watts (Respectively of KVA rating) |  |
| 13. | Load loss at 750 C | Maximum 3180, 1635 & 810 Watts (Respectively of KVA rating) |  |
| 14. | Maximum Temperature Rise at full load Over 400C ambient temperature with tap changer in principal position. | a) | 650C for Winding measured by Resistance Method. |
|  |  | b) | 600C for Top Oil measured by thermometer Method. |

### Major Components

H.T Winding:

| Nominal rated voltage | 11 kV |
| --- | --- |
| Maximum system voltage | 12 kV |
| Basic insulation level (minimum) | 75 kV |
| Tap Changer | +1x2.5%, 0, -3x2.5% of rated kV & all fully rated capacity. Tap Changer shall be off load type, manually operated from an external five-position mechanism. |
| Inter phase connection | Delta |
| Bushings | Porcelain, outdoors type with arcing horns of standard gap, mounted on top of tank. Quantity - 3 Nos. |
| Power frequency withstand voltage for one minute | 28 kV |

L.T. winding:

| Nominal rated voltage | 415 volts |
| --- | --- |
| Highest system voltage | 457 volts |
| Inter phase connection | Y (Wye) with neutral brought out. |
| Bushings | Porcelain, outdoor type, mounted on the top or side (Longest side) of tank. Quantity – 4 nos. |
| Power frequency withstand voltage for one minute | 2.5 kV |

| Transformer Oil: |  |
| --- | --- |
| Application | Insulating mineral oil for Transformer. It will be free from PCB (Poly Chlorinated Biphenyl) |
| Grade of oil | Class-1 |
| a) Physical Properties |  |
| Appearance | Liquid and free from suspended matter or sediment |
| Density at 200 C | 0.895 g/cm3 (Maxm.) |
| Flash point (Closed cup) | 1400 C (Minm.) |
| Kinematics Viscosity at -300 C | 1800 mm2s-1 (Maxm.) |
| Kinematics Viscosity at 400 C | 40 mm2s-1 (Maxm.) |
| Pour point | 400 C (Maxm.) |
| b) Electrical Properties |  |
| Dielectric Strength at 50 Hz (with 2.5 mm standard gap and 40 mm standard depth) | New untreated oil, shall go through filtration treatment before the oils are introduced into the apparatus or equipment. The break down voltage of this oil shall be more than 50 kV. |
| Loss tangent/Dielectric dissipation factor at temp. 900 C, stress 500V/mm to 1000 V/mm and frequency 40 Hz to 62 Hz. | 0.005 (Maxm.) |
| c) Chemical Properties |  |
| Neutralization value | 0.03 mg KOH/g (Maxm.) |
| Neutralization value after oxidation | 0.40 mg KOH/g (Maxm.) |
| Total sludge after oxidation | 0.10% weight (Maxm.) |
| PCB Content | Free from PCB (Poly Chlorinated Biphenyl) |
| d) Standards | Performance and testing of oil shall comply with the latest revision of the relevant standards BS 148 : 1972, IEC-60296 or latest revision there on. |

## FEATURES AND ACCESSORIES

a)	All bolts and nuts connected with transformer tank, conservator, radiator etc. shall be of non-ferrous metal. If it is ferrous metal, it shall be hot dip galvanized as per standard ASTM A90/ BS EN ISO 1461:1999.

b)	Lugs for lifting & towing complete unit.

c)	Facilities for lifting core & coil assembly.

d)	Base designed for platform mounting on poles.

e)	First filling of new oil shall comply to the latest revision of IEC-60296 standard or other equivalent standards.

f)	Each H.T. bushing shall have bolted type bimetallic connector suitable for accommodating ACSR conductor having Dia. range from 9mm to 14.5mm.

g)	Each L.T. bushing shall have bolted type bimetallic connector for accommodating copper/AAC of area range 2x95mm2 to 2x120mm2 depending upon the KVA rating of the transformer.

h)	The L.T. bushing shall be installed on the top or side of tank lengthwise of the transformer body.

i)	Dial type Oil temperature indicator with maximum pointer (red color) to be mounted on L.T. side of the tank.

j)	Earthing terminals at the bottom corners of Tank.

k)	Name plate with transformer rating & winding diagram made of stainless steel shall have engraved letters filled with black enamel and shall be continuously welded in the transformer body.

l)	The tank & radiator or flanged radiator shall be painted with two coats of gray finishing paint on suitable prime coats.

m)	Transformer capacity with Sl. No. and BPDB Contract No. should be marked with emboss/ engrave on the transformer tank adjacent to name plate easily visible from ground as per tender clause-7.14.6.

For Conservator:

a) 	Transformer tank completes with covers, necessary openings & gaskets.

b)	Complete oil preservation system consisting of an oil conservator with shut-off valve oil level gauge. The system shall have valve for filter press inlet & oil drain. The oil sampling valve & dehydrating breather shall be provided.

## INFORMATION REQUIRED

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

- Manufacturer’s Printed Catalogue describing specification and technical data for crucial components of offered 11/0.415KV, 3-Phase, Dyn11 distribution transformer.

- Detail dimensional drawings of offered 11/0.415KV, 3-Phase, Dyn11 distribution transformer.

- The Bidder/ Manufacturer shall submit the list of available testing/ measuring equipment, meters, etc., along with valid Calibration Certificate(s) from competent authority used in manufacturer's laboratory for performing Routine Test as per IEC standard.

- Manufacturer's valid ISO 9001 Certificate.

## TEST REPORTS

Tenderer's shall include in their offer the following routine tests, type tests and Short circuit withstands tests as prescribed in IEC-60076 for 11/0.415KV, 250KVA, 3-Phase, Dyn11 Distribution Transformer.

Routine Tests

1)	Measurement of turn ratio test.

2) 	Vector group test.

3) 	Measurement of winding resistance.

4) 	Measurement of insulation resistance.

5) 	Measurement of no-load loss & no-load current.

6) 	Measurement of impedance voltage & load loss.

7) 	Dielectric withstands Tests.

8) 	Transformer oil tests.

Type Tests

1) 	Impulse Voltage withstands test.

2)	Temperature rise test.

Special Tests

1) 	Short circuit withstand test and detail calculation along with thermal & mechanical on the basis of design data.

## Transformer Construction

General

The transformers shall be double-wound, oil immersed naturally air cooled and conventional type with tank breathers.

The core shall be high-grade cold rolled electrical sheet steel. The primary and secondary windings shall be constructed form high conductivity copper. All turns of windings shall be adequately supported to prevent movement. In cases where turns are spaced out, suitable inter-turn packing shall be provided.

No material, which can be deleteriously affected by the action of oil under the operating conditions of the transformers, shall be used in the transformers or leads or bushings. Construction features shall permit local repairs to be easily carried out in the event of equipment failure.

Transformer Tank

The transformer tank shall be fabricated from steel and be of robust construction; all welds shall be made by the electrical arc welding process and the slag carefully removed after each run.

With the exception of radiator elements, all external joints shall be welded properly. Cooling radiators shall be of robust and simple construction. Complicated shapes shall not be acceptable, and horizontal stiffeners on tanks should be avoided. The bearing surface of the tank to which bushings are clamped shall be substantially flat.

All matching faces or joints to be made oil tight shall be finished with a smooth surface to ensure that the gasketing material will make a satisfactory joint material will make a satisfactory joint.

Flanges and covers of tanks shall be of sufficient thickness to prevent any depression occurring, which would retain water around the bolts.

Bolts shall be spaced at sufficiently close intervals to avoid buckling of either flange or covers and provide reasonably uniform compression of the gasket.

Each transformer shall be provided with a minimum of two closed lifting lugs. The minimum diameter of the hole or width of the slot shall be 25 mm. The two lifting lugs shall be located such that there will be a minimum of 50 mm between the lifting chain and the nearest part of the bushings.

All transformers shall be suitable for outdoor mounting on pole platforms and shall have four mounting lugs with 19 mm dia holes suitable for bolting the transformer to the platform. The two lifting lugs shall be located 150 mm on each side of the centre line of the longest sides of the transformers.

The oil conservator shall be fitted with oil draining and oil filling gate valves, and a breather. The breather shall consist of a looped pipe fitted to the top of the transformer.

The LT Bushings shall be mounted on one of the longest side of the transformer tank. An oil level sight glass shall be fitted and marked with minimum & maximum oil level mark at ambient temperature.

All the transformer shall have the hole (dia 3mm) on the top cover and tank in 2 (two) corners for sealing purpose.

Transformer Core And Coils

Transformers core and coils must be new, unused, and clean.

Supporting frames of the core and coils of transformers shall be designed to accommodate variations in tank height.

The core and coil assembly shall have the core and coils rigidly connected to the tank and suitably closed lugs shall be provided for removing the core and coil assembly from the tank.

Transformer Sl. no. should be marked with emboss on the Supporting frames of the core and coils of each transformers minimum in 2(two) places.

Transformer Sealing

A satisfactory lid-sealing gasket shall be provided on each of these transformers to maintain the seal at extremes of operating temperature. A cold oil level (COL) mark shall be provided inside each transformer marked COL.

Finishes

a) Painting

Painting ferrous metal work is to be provided with an effective vapor sealing paint finish, applied generally in accordance with BS 5493 and /or other recognized international standard.

Paint shall be applied to produce a uniform film. Edges corners, crevices, welds, bolts, and rivets shall receive special attention to maintain the required thickness.

Before painting or filling with oil or compound, all un-galvanized parts shall be completely clean and free from rust, scale and grease and all external rough metal surfaces on the casting shall be filled.

The paint system shall be in accordance with best practice for hot and humid locations in a highly aggressive environment. A description of the paint system to be used and the proposed method of application shall be fully described in the Tender.

All external surfaces shall receive a minimum of three coats of paint. The primary coat shall contain an approved rust inhibitor and shall be applied as soon as possible after the completion of the surface preparation. The second coat shall be of oil and weather resisting nature and have a shade of colour easily distinguishable from the primary. The final coat shall be of oil and weather resisting and non-fading glossy paint of a colour agreed by the Engineer.

b) Non-ferrous parts and Bright Steel parts

All exposed metal liable iron corrosion during transport is to be appropriately protected by casting with an approved anti-rusting composition. Other non-ferrous parts shall be adequately protected against corrosion during shipment or in service.

c) Galvanizing

Galvanizing where applicable shall be applied by the hot dipped process generally in accordance with ASTM A90/ BS EN ISO 1461:1999 or equivalent standard of metal surface unless specified otherwise.

The zinc coating shall be smooth clean and of uniform thickness and free from defects. The preparation of galvanizing itself shall not adversely affect the mechanical properties of the coated material.

All drilling, punching, cutting, shaping and welding of parts shall be completed and all burrs shall be removed before the galvanizing process is applied.

Surfaces that are in contact with oil shall not be galvanized or cadmium plated.

Rating Plate

A brass or stainless-steel rating plate shall be fitted to each transformer. The information shall deeply etch including the diagram of the connections of the windings, the vector diagram showing the general phase relations of the transformer, and a diagrammatic plan of the transformer cover showing the terminal positions and marking and other essential particulars. The plate shall be mounted in an accessible position and preferably adjacent to the tapping switch if this is located on the side of the tank.

The rating plate shall be fitted below the LV terminals. Rating and diagram plates shall be attached by a 5 mm brass screw in each corner to 20 mm mild steel brackets continuously welded horizontally approximately 20 mm from the tank side. The following information is to be provided on the rating and diagram plate in the English language – clearly and indelibly marked.

٭	Transformer type

٭	Manufacture’s name and country of origin

٭	Manufacturer’s serial number

٭	Year of Manufacture

٭	Number of phases

٭	Rated power

٭	Rated frequency

٭	Rated voltages

٭	Rated currents

٭	Connection symbol

٭	Impedance voltage at rated current

٭	Type of cooling

٭	Total mass

٭	Mass of insulating oil

٭	Insulation levels

٭	Details regarding tapings

Each Transformer should be marked with emboss or welded on the body easily visible from the ground, with letters of size mentioned against each word(s)/ sentence(s) below:

BPDB (40 mm)

Contract No & Date: (20 mm)

Country of Origin:

Sl. No.: --------- of ------------KVA ---------- (20 mm)

Note:

a) 	Sl. No. ......................of ..............KVA ...... is meant for particular No. of the Transformer out of the contracted quantity under this contract.

b) 	The above marking on the body of the transformer shall be done in addition to the normal nameplate of the transformer. The nameplate shall be continuous welded on the body of the Transformer before Pre-delivery inspection.

Terminal Marking

All transformers shall have the primary and secondary terminal markings plainly and indelibly marked on the transformer adjacent to the relevant terminal. These markings shall preferably be 25 mm in height. The terminal marking shall be embossed on the body of the Transformer with respective color code.

Terminal Leads

Outgoing leads shall be brought out through bushings. The leads shall be such that the core and coils may be removed with the least possible interference with these leads, and they shall be specially supported inside the transformer to withstand the effects of vibration and short circuits.

Bushings

All bushings shall be porcelain clad, and shall be of the highest quality. They shall be sealed in a manner to prevent ingress of moisture and to facilitate removal. The neutral bushings and stems shall be identical to those provided for phase terminations. Bushing stems, nuts and washers shall be made of brass.

Earthing Connections

Earthing connections shall be provided with connection facilities for 2x50 mm2 copper stranded conductor. The bolts shall be located on the lower side of the transformer and be of M12 size; each shall be clearly indicated with an engraved ‘earth symbol’. Two earthing connections are required on each transformer.

Gaskets

Any gaskets provided with the transformers shall be suitable for making oil tight joints, and there shall be no deleterious effects of either gaskets or oil when the gaskets are continuously in contact with hot oil. No gaskets shall be used in which the material of the material of the gasket is mounted on a textile backing. Exterior gaskets shall be weatherproof and shall not be affected by strong sunlight. All gaskets shall be closed design (without open ends) and shall be one piece only.

Oil

All transformers shall be filled to the required level with new, unused, clean, standard mineral oil after treatment in compliance with IEC 60296 & BS 148.

Tapings

Five voltage tapings shall be provided on the primary side of each transformer and shall give: + 2.5%, 0,- 2.5%, – 5% and –7.5% steps of the primary nominal voltage.

The tapings shall be selected by an ‘off load’ tapping switch with an external hand wheel with provision for looking onto a selected tapping. The switch shall have a positive action designed to eliminate the possibility of stopping in an intermediate position. The shaft shall be adequately sealed so that no seepage of oil occurs under all conditions of service.

The voltage operating positions, together with tap change positions shall be clearly and indelibly marked.

19.0 Technical Specifications of Overhead –Type Single Phase Distribution Transformers

## Scope

This standard covers the electrical, mechanical and performance requirements for single phase, mineral-oil-filled, overhead type distribution transformers for use on 11,000/6350 GRD "Y" volt BPDB overhead distribution system.

## General

Distribution transformers furnished to BPDB specifications shall conform in all respects to the requirement of this standard. These transformers will be used in a tropical climate with high annual rainfall.  The text, tables, figures and references to other standards supplement each other and are considered of this standard.

## Ratings

Nominal voltage ratings

a.	H.V. winding - 6350 volts

b.	L.V. winding - 240 volts

Basic insulation levels

a.	H.V. winding - 95 KV

b.	L.V. winding - 30 KV or as per latest ANSI requirement.

Frequency - 50 Hertz

Percent impedance shall be

a.	2.5% for 5 KVA to 37.5KVA.

b.	3% for 50 KVA to 167 KVA.

Note: Percentage impedance may vary up to +10%.

Ambient air temperature is 40°C. Average winding temperature rises above ambient shall not exceed 65°C when measured by the resistance method. The hottest spot temperature rise of the winding shall not exceed 80°C over ambient.  Temperature rise of the insulating liquid shall not exceed 65°C when measured near the top of the tank. Temperature limits shall not be exceeded when the transformer is operating at rated KVA output and rated secondary voltage for 24 (twenty-four) hours.

Transformers with ratings of 200 KVA or less shall have additive polarity; transformers with ratings over 200 KVA shall have subtractive polarity.

KVA ratings shall be as shown in Table 1.

## Design:

Transformers shall be designed in accordance with the revision (revision from 2010 to the latest revision) of the following ANSI standards: ANSI C57.12.00, ANSI C57.12.20

Transformers shall be class OA, (Self-cooled) wound core and have two windings of high conductivity copper. Transformer Core shall be of Cold Rolled Grain Oriented Silicon Strip Steel (CRGO)/Amorphous.

H.V. Bushings:

a. 	Outdoor type porcelain. The bushing should be easily replaceable & fitted with Corrosion resistant bolts, nuts & gaskets.

b.	Connectors shall be bolted ring type, suitable for copper or aluminium. Connectors shall accommodate the range of conductor sizes indicated in Table-1.

c. 	Connectors shall be bird-proof with a rubber like insulating cover.

d.	Transformers rated 200 KVA or less shall have one (1) H.V. bushing mounted on the cover of the tank.  All transformers rated over 200 KVA shall have two (2) H.V. bushings mounted on the cover of the tank.

L.V. Bushings:

a.	Outdoor type, porcelain.  The bushing should be easily replaceable & fitted with corrosion resistance bolts, nuts & gaskets.

b.	Connectors shall be in accordance with Table 1. Where bolted ring type connectors are used they shall be suitable for use with copper or aluminium and shall accommodate the range of conductor sizes as indicated in Table 1.

c.	There shall be two (2) L.V. bushings mounted on the side of the tank.

Tank

- Transformer tank shall be sealed type design complete with cover and gaskets.

- Tank shall be supplied with a tank grounding bolted ring-type connector suitable for use with copper or aluminium.  The connector shall have a range of #6 to #3 AWG.

- There shall be a low voltage grounding provision with a removable copper strap.

- Tank shall have permanent lugs for lifting the complete unit.

- There shall be facilities for lifting the core and coil assembly.

- Tank shall be equipped with a self-sealing pressure release device designed to operate at a minimum gage pressure of 0.564 Kg/cm2 (8 lb / inch2)

- Tank shall be painted with two coats of light grey paint, ANSI colour #70 over a suitable primer coat.

- The letters “BPDB” shall be painted in 7.62 centimetre (3") letters in front of the tank.

- Nameplate shall be made of stainless steel and shall have engraved letters filled with black enamel.  Nameplate information must include, but is not limited to, the following:

Contract number and IFB number

Serial Number

Class

Number of phases

Frequency

Voltage Rating

KVA ratings

Ambient temperature

Temperature rise, degree C

Polarity

Percent impedance

Approximate total mass in pounds & kilograms

Connection diagram

Name of manufacturer

Date of manufacture

Installation and operating instructions reference

The word “Transformer”

Type of insulating liquid (generic name preferred)

Conductor material (of each winding)

- Tank shall have supporting lugs in accordance with the designations in Table-1.

- Rating in KVA shall be painted in 7.62 centimetre (3") letters in front of the tank.

- Transformer serial number shall be painted (2") letters in black 1800 opposite to transformer hanger bracket centre line & 1" clear bottom of tank.

- The bottom of the Tank should be one (l) inch above the Transformer bottom.

Insulating Oil

Insulating oil shall be new, unused mineral (non-PCB) oil and meet the requirements of ANSI/ASTM D3487-79.  A suitable marking inside of the tank shall indicate oil level at 250C. The active part (Core &Coil) of the Transformer shall be submersed within oil and sufficient air space shall be provided.

| Transformer Oil |  |
| --- | --- |
| Application | Insulating mineral oil for Transformer |
| Grade of oil | Class-1 |
| PHYSICAL PROPERTIES |  |
| Appearance | Liquid and free from suspended matter or sediment |
| Density at 200C | 0.895g/cm3 (maximum) |
| Flash point (Closed cup) | 1400C (minimum) |
| Kinematics Viscosity at-150C | 800 cst. (Maximum) |
| Kinematics Viscosity at-200C | 40 cst. (Maximum) |
| Pour point | -300C (maximum) |
| ELECTRICAL PROPERTIES |  |
| Dielectric Strength at 50 Hz (with 2.5 mm standard gap and 40 mm standard depth) | On new untreated oil, the break down voltage shall be at least ≥30KV. |
| Loss tangent/ Dielectric dissipation factor at temp 90̊ C, stress 500V/ mm to 1000 v/ mm and frequency 40 Hz to 62 Hz. | 0.005 (maximum) |
| CHEMICAL PROPERTIES |  |
| Neutralization value | 0.03mg KOH/g (maximum) |
| Neutralization value after oxidation | 0.40mg KOH/g (maximum) |
| Total sludge after oxidation | 0.10% weight (maximum) |
| PCB Content | Free from PCB |

Lock washers

All electrical connections, bushing mounting bolts and cover attachment bolts require lock Washers.  Lock Washers shall be fabricated from materials that comply with the requirements of ANSI B18.21.1.

Bolts

The bushing mounting bolts and cover attachment bolts must be fabricated from steel that complies with the requirement of ANSI standard C 135.1. The bolts, Lock washers and Nuts if used shall be hot-dip galvanised in accordance with ASTM A 153.4.9

Gaskets

Gaskets of nitrile rubber shall be used to ensure perfect oil tightness and there shall be no deleterious effects of either gaskets or oil when the gaskets are continuously in contact with hot oil. All gaskets shall be closed design (without open ends) and shall be one piece only. Exterior gaskets shall be weatherproof and shall not be affected by strong sunlight. Care shall be taken to secure uniformly distributed mechanical strength over the gaskets and retains throughout the total length. No gaskets shall be used in which the material of the gasket is mounted on a textile backing. Gaskets of neoprene or any kind of impregnated/ bonded core or cork only which can easily damage by over pressing is not acceptable. Use of hemp as gasket material is also not acceptable.

## TESTS

All tests shall be carried out as per ANSI Standard C57.12.90 (revision from 2010 to the latest revision) in a reputed independent testing laboratory.

Routine tests:

The following routine tests shall be conducted at the factory on all transformers.

- Resistance measurement of all windings

b.	Ratio test

c.	Polarity and phase relation test

d.	No-load losses at rated voltage and rated frequency

e.	Excitation current at rated voltage and rated frequency

f.	Impedance voltage and load loss measurement

g.	Induced high voltage test

h.	Power frequency withstand test

i.	Dielectric tests of oil

j.	Loss tangent / Dielectric dissipation factor test of oil

k.	* Lightning impulse test

l.	** Temperature Rise Test

*Note 1: KVA rating wise one sample from the daily production lot.

** Note 2: KVA rating wise two samples from a lot/batch will be tested for Temperature rise.

Type Tests:

a. 	Lightning Impulse test

b. 	Temperature Rise test

c. 	Short Circuit withstand test

Note: These all type tests shall be done on same Transformer (having same serial no.)

The losses of the transformers at 85°C will be limited (loss tolerances are not applicable) as stated below:

| Ratings (in KVA)/Loss (in Watt) | 5 KVA | 10 KVA | 15 KVA | 25 KVA | 37.5 KVA | 50 KVA | 75 KVA | 100 KVA | 167 KVA |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No-load Loss (in Watt) | 19 | 25 | 35 | 46 | 65 | 75 | 115 | 140 | 240 |
| Full-load Loss (in Watt) | 120 | 190 | 250 | 380 | 480 | 600 | 860 | 1120 | 1900 |

## SPARE PARTS:

The Bidder shall include separately with his Tender a list of recommended spare parts with per unit price quoted for each item. The list shall include, but not be limited to, the spares listed below:

a.	One complete set of all gaskets.

b.	One complete H.V. bushing.

c.	One complete L.V. bushing.

## INFORMATION REQUIRED

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

- Manufacturer’s Printed Catalogue describing specification and technical data for crucial components of offered 1-Phase distribution transformer.

- Detail dimensional drawings of offered 1-Phase distribution transformer.

- The Bidder/ Manufacturer shall submit the list of available testing/ measuring equipment, meters, etc., along with valid Calibration Certificate(s) from competent authority used in manufacturer's laboratory for performing Routine Test as per ANSI standard.

- Manufacturer's valid ISO 9001 Certificate.

## TEST REPORTS

Tenderer's shall include in their offer all routine tests and type tests as per ANSI standard C57.12.90 (revision from 2010 to the latest revision) from an reputed  Independent Testing Laboratory for 1-phase Distribution Transformer as per clause no. 7.5 . All type tests shall be done on same transformer (having same serial no.) from reputed independent testing laboratory.

## PACKAGING:

- Lumber used in the fabrication of shipping/delivery crates shall be new, sound, well seasoned and free of knots and decay.

- Crates shall be provided with a skid base.  Transformers shall be strapped, bolted, braced or secured to the crate base during shipment and handling.

- Particular attention shall be given to protection of the porcelain bushings during shipment.

- Crates shall be sufficiently strong to prevent damage from stacking and handling.

## OTHER STANDARDS:

(i) 	The physical and performance requirements of distribution transformers based on other international recognised standards are acceptable only if the requirements of such standards are equivalent to or exceed the requirements quoted in this document.

(ii) 	Drawing, design and dimensions will be applicable as per entities’ requirement.

TABLE-1

## TRANSFORMER

| KVA Rating | H.V. Bushing | L.V. Bushing | Support | Polarity |
| --- | --- | --- | --- | --- |
|  | Conductor Range | Conductor Range | Lug Type |  |
| 5 | 6 solid – 3 ACSR | 6 solid-1/0 ACSR | A | Additive |
| 10 | 6 solid – 3 ACSR | 6 solid-1/0 ACSR | A | Additive |
| 15 | 6 solid – 3 ACSR | 6 solid-1/0 ACSR | A | Additive |
| 25 | 6 solid – 3 ACSR | 6 solid-4/0 ACSR | A | Additive |
| 37.5 | 6 solid – 3 ACSR | 6 solid-4/0 ACSR | A | Additive |
| 50 | 6 solid – 3 ACSR | 6 solid-4/0 ACSR | A | Additive |
| 75 | 6 solid – 3 ACSR | 2 solid-4/0 ACSR | B | Additive |
| 100 | 6 solid – 3 ACSR | 2 solid-4/0 ACSR | B | Additive |
| 167 | 6 solid – 3 ACSR | Spade H | B | Additive |

TABLE-2

DIMENSION OF THE TRANSFORMER TANK

| KVA RATING | MINIMUM DIAMETER OF TANK | MINIMUM HEIGHT OF TANK |
| --- | --- | --- |
| 5 | 12"(305mm) | 22"(559mm) |
| 10 | 13.5"(338mm) | 24"(610mm) |
| 15 | 15"(381mm) | 26"(660mm) |
| 25 | 16"(406mm) | 29"(737mm) |
| 37.5 | 18"(457mm) | 32"(813mm) |
| 50 | 20"(508mm) | 36"(914mm) |
| 75 | 22"(559mm) | 38"(965mm) |
| 100 | 24"(610mm) | 40"(1016mm) |
| 167 | 26"(660mm) | 44"(1118mm) |

## BIBLIOGRAPHY OF REFERENCE STANDARDS, (revision from 2010 to the latest revision)

1.	ANSI C57.12.00	:	General requirements for overhead-Type Distribution and Power Transformers.

2.	ANSI C57.12.20	: 	Requirements for Overhead-Type Distribution Transformers 6700 Volts and Below 500 KVA and Smaller.

3.   	ANSI C57.12.90	:	Test Code for Liquid Immersed, Distribution, Power and Regulating Transformers.

4.	ANSI B18.21.1	: 	Lock Washers.

5.	ANSI C 135.1	: 	American National Standard for Galvanized Steel Bolts and Nut for Over Head Line Constructions.

6.	ANSI C 135	: Standard Specification for Zinc Coating (Hot-Dip) or iron and steel Hardware.

20.0 Technical Specifications/ Requirements of Transformer Platform Structure

Standards

The equipment specified in this section shall conform to the latest edition of the appropriate IEC specifications and other recognized international standards. In particulars

BS EN ISO           Hot dip galvanized coatings on fabricated iron and steel articles.

1461:1999

ASTM A90	Standard test method for weight of coating on Zinc-coated (galvanized) iron or steel 		articles.

BS 4190:1967 	Isometric Hexagonal Bolts, Screws and Nuts.

BS 4360		Specification for weld able Structural Steel

BS 4870		Specification for approval testing of welding procedures.

BS 5757		Quality Assurance.

# If the Bidder offers other equivalent standards full details including copies in English Language of such standards shall be submitted with the offer.

# Technical Specification

General

This specification includes the design, manufacture, and testing of SPC Pole fittings.

Definitions and Abbreviations

The following definitions and abbreviations apply to the specification.

Definitions:

| i) | Failure | : | Inability of the pole fittings when under test to support further load or when deformation or buckling of the pole renders it unserviceable. |
| --- | --- | --- | --- |
| ii) | Longitudinal direction | : | The horizontal direction parallel to the run of the direction of the conductors. |
| iii) | Transverse direction | : | The horizontal direction at right angles to the run of direction of the conductors. |
| iv) | Ultimate Tensile Strength | : | The strength at which the pole fittings will not accept any further applied force or when deformation or buckling or the pole renders at unserviceable. |

Abbreviations

BS	: 	British Standard.

IEC	:	International Electro-technical Commission

Mpa	:	Mega Pascal = 1 N/sq. mm.

Material and Manufactures

Manufacturer’s test certificates for material strength shall be supplied to the Engineer/ Purchaser at the time sample approval. The test certificates shall show compliance with the relevant standard specifications in all respects. If the manufacturer’s test certificates are not available or if the Engineer/ Purchaser requires it then the supplier/ manufacturer is responsible for arranging all testing requested by the Engineer/ Purchaser.

The test information so obtained must be sufficient to satisfy the Engineer/ Purchaser that the item being tested conforms to the relevant standard specification.

Materials for Pole fittings

All materials shall be new and conform to the relevant standard referred in these specifications. All types of pole fittings and accessories shall be manufactured from material having minimum yield strength of 245 N/sq. mm as per BS 4360.

Corrosion Protection and Galvanizing

a) 	All pole fittings, including Nuts and Bolts, shall be hot-dip galvanized in accordance with BS 729: 1971.

b) 	The zinc coating shall be smooth, clean and of uniform thickness and free from defects. All drilling, punching, cutting, shaping and welding of parts shall be completed and all burns shall be removed before the galvanizing process is applied.

c) 	Any galvanized surface of the pole fittings damaged after delivery and within the warranty period shall be scrapped back to a firm base and two full thickness and coats of Zinc rich primer applied to the damage to the galvanizing is extensive then that pole fittings shall be removed from site and re-galvanized.

Marking of Pole Fittings

Drawing number along with marking number (marking will be provided during sample approval) to be embossed or engraved directly on the all pole fittings. Dimensions/Diameter also marked if same drawing number’s fittings have different dimensions.

Design of Pole Fittings and Sample(s) Approval

The fittings shall be so designed that they fit with the specified poles. According to this, the samples manufactured as per the approved drawings shall be submitted to the engineer for getting the concurrence on going to the mass production of the same. Before full scale manufacture is commenced, two samples of each type of fitting shall be prepared for examination and approval by the Engineer. Production items not meeting the same standard as the initial samples approved by the Engineer will be rejected.

Dimensional Tolerances

The permitted variation from stated dimension shall be as follows except mentioned otherwise.

Material sizes		:	+/-1 mm.

Thickness tolerance	:	-0%, +10%.

Manufacture

Pole fittings shall be manufactured to the details on the attached drawings and schedules and from the materials specified in this section.

All welding of the pole fittings shall be carried out in accordance with the procedures of an international standard approved by the Engineer and these procedures shall be tested in accordance with AWS standards at the manufacturer’s plant and before galvanization. All welding shall be continuous and shall be of a size and type capable of developing the full strength of the parent metal without permanent distortion in the finished fittings.

Quality Assurance

The manufacturer shall maintain the quality assurance practices that will be applied to all aspects of the pole fittings manufacturing process, which conforms generally to the requirements of BS 5757: 1979 or equivalent standards.

Drawings

All drawings of Pole Fittings are included. Poles may not have provision of holes for fixing the Pole Fittings. All sorts of Pole fittings shall be fixed by using clamps. Fixing arrangement of Pole Fittings with the pole shall be done according to the profile of the poles offered at different position of Poles. However the Supplier/ Manufacturer shall be responsible for ensuring overall fixing the Pole Fittings. The Supplier/ Manufacturer shall submit all the drawings of pole fittings to the Engineers for approval before manufacture.

BILL OF MATERIALS, BILL OF QUANTITIES AND DRAWINGS OF PLATFORM

FOR DISTRIBUTION TRANSFORMER:

- Transformer Base Angle		2 (two) Pcs.

- Fuse Mount Channel			1 (one) Pc.

- Transformer Base Bracing Angle	4 (four) Pcs.

- J Bolt					4 (four) Pcs.

- Clamp for Bracing			2 (two) Pcs.

- Clamp for Fuse Mount Channel		2 (two) Pcs.

- Pole Band				4 (four) Pcs.

- Nuts & Bolts				As per drawing

### 21.0 TECHNICAL DESCRIPTION OF 11 KV DROP OUT FUSE CUT OUT (DOFC)

### RATINGS

Distribution fuse cutouts shall have ratings as defined in IEC Standard and as summarized below:

Rated Voltage:

a.	Nominal System Voltage – 11kV (L-L) /6.35kV(L-N)

b.	Rated Maximum Voltage –15 kV

c.	Power Frequency Withstand KV, RMS -

dry, 60 sec. –28 kV

wet, 10 sec. –32kV

Rated Impulse Withstand Voltage - 75 KV.

Rated Frequency - 50 Hz.

Rated Continuous Current - 100 A.

Rated Short Time Current

a.	Momentary (1 cycle) - 10,000 A

b.	15 cycles - 7,100 A

c.	3 seconds - 1,600 A.

Rated Symmetrical Interrupting Current - 7,100 A.

### DESIGN

Distribution fuse cutouts furnished to BPDB specifications shall be designed and manufactured in accordance with IEC 60282. The cutouts are intended for use with button-type fuse links meeting the standards of IEC Publication 60282. The country of origin of DOFC shall be same as the place of manufacture. Figure 1, 2 and 3 shows a conceptual arrangement and nomenclature of a distribution fuse cutout. These cutouts shall have the following design features. All Fitting shall be same as per attached drawing. Deviation is not accepted.

### Fuse Support Assembly

- Fuse Support Insulator – Wet process Porcelain/ Polymer (Hydrophobic silicon) and shall be suitable to withstand a mechanical force of minimum 1.6 KN.

- Markings-

Manufacturer's Identification Product Type

Date of Manufacture

Rated Continuous Current

Rated Maximum Voltage

Rated Interrupting Current

Basic Insulation Level

Contract No/IFT No.

- Contacts Materials – Brass.

- Connectors Materials - Brass type, suitable for AAC/ACSR/Copper conductor of diameter from 10 mm to 15 mm.

- Load-buster tool attachment hooks.

- Mounting Supports - suitable for using with the mounting bracket provided to mount the cut-out so that the centerline of the fuse support insulator is at an angle of 15 degree to 20 degree from the vertical.

- Contact Plate Holder Assembly - Hot dip-galvanized and corrosion free.

### Fuse Holder Assembly

- Fuse Tube –The inner side of the Fuse Tube shall be bone fiber lining with exterior painted gray, non-expendable cap. Inner and Outer diameter should be 15mm±0.2mm and 30mm±0.2mm respectively. Inner surface bone fiber of the barrel should be smooth and non flammable. Any rough surface is not acceptable.

- Contacts Materials – Brass. The dimensions shall be as per figure 1 to 6.

- Fuse Link Position - the fuse tube shall be designed so the fuse link is centered and uniform in the tube, with provision for mechanical ejection of the fuse link lead even on low current faults.

- Opening and Lifting Eyes - the fuse holder shall hang vertically from the fuse support assembly when in the open position, and shall have opening and lifting eyes suitable for removal and installation of the assembly, and opening and closing of the cutout with a switch stick described in IEC 60282.

- Thumb Screw –Thumb screw shall be butterfly type and it shall be used for securing the fuse link to fuse holder assembly.

- Thumb screw bolt- It shall be fixed with the fuse holder assembly.

- All spring, nuts, bolts between contact plate and assembly unit shall be non-magnetic & corrosion free.

### Mounting Bracket

Each distribution fuse cutout shall be provided with a mounting bracket meeting the requirements of IEC Standard. The mounting bracket shall be adjustable to accommodate standard cross arms. The mounting bracket, machine bolts and compatible standard square nuts and lock-washers shall be hot-dip galvanized in accordance with BS 729.

### Lock Washers

All mounting bolts and conductor connectors require lock washers. Lock washers shall be fabricated from material that comply with the requirements of BS 729.

### TEST REPORTS:

Tenderer's shall include in their offer the following tests as prescribed in IEC-60282 for offered type DOFC of same voltage class:

### Type Test:

- Dielectric Tests.

- Mechanical Test

- Breaking Test

- Test for time/current characteristics

- Temperature Rise Tests.

### Special Test:

- The randomly selected samples shall be sunk in the water tank for minimum twenty four (24) hours. After removing samples from the water tank, inner diameter of the fuse tube shall be reduced by minimum 1.0mm. Also the inner surface shall be smooth and regular after removal from the tank.

- Inside the fuse link tube of the randomly selected samples, a flame will be ignited but inside of the tube shall not be flammable.

Type test report as per clause no. 5.0(a) for offered type DOFC of same voltage class as per IEC 60282. All Type Test shall be done from any of the following independent testing laboratories:

  - CESI

  - ESEF ASEFA

  - JSTC

  - KEMA

  - PEHLA

  - TUV Rheinland

  - SATS

  - STLNA

  - VEIKI

  - ZKU

  - UL

22.0 TECHNICAL SPECIFICATION OF FUSE LINK

STANDARDS

Performance, Design & Testing of Fuse Link shall conform to the latest edition of the ANSI Standard or equivalent international Standards unless otherwise specified herein.

TABLE-1

Melting Currents for Type-K (Fast) Fuse links*

| Rated Continuous Current | 300 or 600 Second Melting Current* |  | 10 Second Melting Current |  | 0.1 Second Melting Current |  | Speed Ratio |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum |  |
| PREFERD RATINGS |  |  |  |  |  |  |  |
| 6 | 12.0 | 14.4 | 13.5 | 20.5 | 72 | 86 | 6.0 |
| 10 | 19.5 | 23.4 | 22.5 | 34 | 128 | 154 | 6.6 |
| 15 | 31.0 | 37.2 | 37.0 | 55 | 215 | 258 | 6.9 |
| 25 | 50.0 | 60.0 | 60 | 90 | 350 | 420 | 7.0 |
| 40 | 80.0 | 96.0 | 98 | 148 | 565 | 680 | 7.1 |
| 65 | 128.0 | 153.0 | 159 | 237 | 918 | 1100 | 7.2 |
| 100 | 200.0 | 240.0 | 258 | 388 | 1520 | 1820 | 7.6 |
| 140 | 310.0 | 372.0 | 430 | 650 | 2470 | 2970 | 8.0 |
| 200 | 480.0 | 576.0 | 760 | 1150 | 3880 | 4650 | 8.1 |
| INTERMEDIATE RATINGS |  |  |  |  |  |  |  |
| 8 | 15.0 | 18.0 | 18 | 27 | 97 | 116 | 6.5 |
| 12 | 25.0 | 30.0 | 29.5 | 44 | 166 | 199 | 6.6 |
| 20 | 39.0 | 47.0 | 48 | 71 | 273 | 328 | 7.0 |
| 30 | 63.0 | 76.0 | 77.5 | 115 | 447 | 546 | 7.1 |
| 50 | 101.0 | 121.0 | 126 | 188 | 719 | 862 | 7.1 |
| 80 | 160.0 | 192.0 | 205 | 307 | 1180 | 1420 | 7.4 |
| RATING BELOW 6 AMPERES** |  |  |  |  |  |  |  |
| 1 | 2.0 | 2.4 | - | 10.0 | - | 58 | - |
| 2 | 4.0 | 4.8 | - | 10.0 | - | 58 | - |
| 3 | 6.0 | 7.2 | - | 10.0 | - | 58 | - |

*   300 seconds for fuse links rated 100 amperes and less, 600 seconds for fuse links rated over 100 amperes.

** No minimum values are specified at 10 seconds or at 0.1 second for fuse links rated at less than 6 amperes. Fuse links rated 1, 2 or 3 amperes shall coordinate with fuse links rated 6 amperes, but not necessarily with each other.

SPECIFICATIONS

| 1 | Installation | Outdoor mounted on 11kV DOFC. |
| --- | --- | --- |
| 2 | Nominal rated voltage (3 phase) | 11 kV |
| 3 | Maximum System voltage (3 phase) | 12 kV |
| 4 | Frequency | 50 Hz. |
| 5 | Fuse holder type | Heavy duty, sealed cap with eye at upper end of the fuse holder. |
| 6 | Fuse link continuous current ratings | 50 amps |
| 7 | Fuse link type | K-type |
| 8 | Standard | ANSI C37.40, C37.41 & C37.42 |

Tests:

Fuse link shall be tested in accordance with ANSI C37.41-1981, Section 11, 12 & 3.4.2.

(i) Temperature rise test shall be conducted for the offered items in accordance with ANSI C37.41 Section 11 (ANSI C37.42, Section 3.3.1)

(ii)Time-Current tests shall be conducted in accordance with ANSI C37.41, Section 12.

- Accuracy – The minimum melting characteristics shall not be less than the minimum values indicated in TABLE-1. The minimum melting current characteristics plus the manufacturing tolerances shall not exceed the maximum values presented in the same table. A sufficient number of tests shall be made to ensure that all fuse links meet these accuracy requirements.

- Presentation of Data – Standard time-current curves, based upon tests made in accordance this standard, shall be furnished with each proposal to furnish fuse links. These curves shall be presented for both minimum melting and total clearing time – current characteristics in accordance with ANSI C37.41, section 12.3.

(iii)-     Impulse test shall be made for the offered items in accordance with ANSI C37.41

Section 3.4.2.

Mechanical Interchangeability:

The diameter of the button head, the size and shape of the fuse links, minimum overall length and thickness of bending sections shall be in accordance with the requirements of Section 3.2.2 of ANSI C37.42.

- Submitted type test report for offered type Fuse Link of same voltage class shall be as per relevant standard. Test shall be done from any of the following independent testing laboratories:

  - CESI

  - ESEF ASEFA

  - JSTC Japan

  - KEMA

  - PEHLA

  - TUV Rheinland

  - SATS

  - STLNA

  - VEIKI

  - ZKU

  - UL

23.0 Technical Specifications of 11kV Outdoor Type Single Phase Metal Oxide Gapless Lightning Arrester

Standards

Performance, Design & Testing of Outdoor Type Single Phase Metal Oxide (ZnO) Gapless Lightning Arrester shall conform to the latest edition of the IEC-60099-4 or equivalent international Standards unless otherwise specified herein.

TECHNICAL REQUIREMENTS

Lightning arrester shall have the following characteristics:

| 1 | Application | Distribution Transformer/ Overhead Line/ Power Cable Line/ Power Transformer of heavy-duty class. |
| --- | --- | --- |
| 2 | Type of Arrester | Station Class, Metal Oxide (ZnO), Gapless |
| # 3 | # Construction | Single Unit, gapless hermetically sealed in with non-linear characteristics with high energy capacity, all enclosed in housing. |
| 4 | Installation | Outdoor |
| 5 | Mounting | Pole Mounted steel bracket |
| 6 | Rated Arrester Voltage (rms, Ur) | 9kV |
| 7 | Continuous Operating Voltage (COV, Uc) | 8- 10 kV |
| 8 | Number of Phase | 1 |
| 9 | Nominal Discharge Current (kAp) of 8/20 micro second wave | 5 kA |
| 10.1 | Type of Lightning Arrester housing | Porcelain/Polymer (Hydrophobic silicon) |
| 10.2 | Core Technology | Open Cage Porcelain/Polymeric |
| 10.3 | Power Frequency withstands voltage of Lightning Arrester Housing, Dry & Wet. | ≥ 35 kV (Dry) & 30 kV (Wet) |
| 10.4 | Impulse Withstand Voltage of Lightning Arrester Housing. | ≥75 kV (peak) |
| 11 | Lightning Impulse Residual Voltage (8/20 micro-second wave) | 35 kV (peak) |
| 12 | High Current Impulse Withstand Value (4/10 micro-second) | 65kV (peak) |
| 13 | Creepage distance (minimum) | 25 mm/ kV |
| 14 | Partial Discharge (pico-coulomb) when energized at 1.05 times its continuous operating voltage. | Not exceeding 10 pC |

BASIC FEATURES

CONSTRUCTION:

Lightning arresters shall be gapless type described briefly as follows:

- Gap less Arresters shall have elements of zinc oxide to perform both the surge discharge and power frequency reseal functions. ZnO arrester shall have excellent thermal stability for high energy surges, external pollution & temporary over voltage.

INSULATORS

The housing insulator of Lightning Arrester shall be wet process porcelain/polymer (Hydrophobic silicon). The insulator sheds shall be designed to minimize the trapping of contamination and shall have a high Creepage distance (minimum 25mm/kV) and a high dielectric strength, as specified in article 1.6 above. Also, the minimum aerial distance between contact terminal to ground shall be 10 inch (254mm) for 11kV.

CONNECTORS

The Line lead and earthing terminal with clamps shall be provided, suitable to accommodate AAC/ ACSR/ Copper Conductor of diameter from 10.0mm to 15 mm.

NAMEPLATE

Information required for identification must be embossed on a stainless-steel nameplate firmly fixed to the arrester and shall include:

a.	Arrester classification

b.	Manufacturers identification or symbol

c.	Arrester model and identification number

d.	Arrester voltage rating

e.	Year of manufacture

f.	Contract Number.

MOUNTING

For pole mounted Mounting steel bracket and fixing bolts, nut, washer, Standard clam etc. shall be provided with the arrester for steel cross-arm. The mounting steel bracket & necessary fittings shall be hot dip galvanized as per BS-729.

For structure mounted surge arrester, arrester shall be supplied with insulating base.

FINISH

All exposed steel or iron parts of the arrester except threaded parts smaller than 3 inch in diameter, shall be hot dip galvanized in accordance with ASTM A153.

TESTS:

TYPE TEST CERTIFICATES:

Tenderer's shall include in their offer the following type tests report as prescribed in IEC60099-4 for offered type Lightning Arrester of same voltage class:

- Insulation withstand test on the arrester housing.

- Residual voltage test.

  - Step current impulse residual voltage test.

  - Lightning impulse residual voltage test.

  - Switching impulse residual voltage test.

- Long duration current impulse withstands test.

- Operation duty test.

  - High-current impulse operating duty test.

  - Switching surge operating duty test.

- Short-circuit test.

- Internal partial discharge test.

- Bending moment test.

- Environmental test.

- Seal leak rate test.

- Radio interference voltage (RIV) test.

ROUTINE TEST:

Manufacturer have all routine test facilities for arrester at their own manufacturers’ premises premises. The following routine tests shall be carried out on all the arresters as per IEC 60099-4 and the test reports shall be made available for the observation at the time of inspection.

- Residual voltage test.

- Internal partial discharge test.

- Reference voltage test.

- Leak test.

SPECIAL TEST:

Following special tests shall be performed during Pre-Shipment Inspection & Inspection at site (if necessary).

  - Insulation resistance test :

Insulation test result shall be more than 1GΩ.

  - Seal Test:

The randomly selected samples as specified shall be sunk in the 1 (one) meter deep water tank for minimum 4 (four) hours. After removing samples from the water tank, the insulation resistance test shall have to perform again.   The insulation resistance test result shall not vary more than 10% before and after seal test. After completing this test the MCOV shall be applied on Arrester at least five times. In each time the result shall be satisfactory as per specification.

Type test report as per clause no. 1.8.1 for offered type Lightning Arrester of same voltage class as per IEC 60099-4. All Type Test shall be done from any of the following independent testing laboratories:

- CESI

- ESEF ASEFA

- JSTC

- KEMA

- PEHLA

- TUV Rheinland

- SATS

- STLNA

- VEIKI

- ZKU

- UL

24.0 Technical Specifications/ Requirements of 1-PHASE MCCB WITH ENCLOSURE

Specification

| 1.0 |  | General: |  |
| --- | --- | --- | --- |
| 1.1 |  | Description | This circuit breaker is required for transformer secondary and or feeder protection. Each unit consists of Molded Case Circuit Breaker (MCCB) mounted in a weather proof enclosure made of galvanized steel sheet of minimum 2mm thickness. Galvanization shall be as per latest revision of ASTM A90/ BS EN ISO 1461:2009 standard. |
| 1.2 |  | Installation | Outdoor pole mounted. |
| 1.3 |  | Climatic condition: |  |
|  |  | a) Temperature (min. to max.) | 3°C to 45°C |
|  |  | b) Relative humidity | 98% |
|  |  | c) Altitude (above sea level) | Up to 300 meters above sea level |
|  |  | d) Atmospheric condition | Moderately polluted |
| 1.4 |  | Minimum protection degree of the unit | IP-55 as per IEC–60529 |
| 2.0 |  | Molded Case 1-Phase Circuit Breaker: |  |
| 2.1 |  | Frame size | 300 Amps / 250 Amps/ 200 Amps |
| 2.2 |  | Rated operating voltage | 230 volts AC |
| 2.3 |  | Rated insulation voltage i.e. maximum system voltage (Ui) | ≥ 690 Volts AC |
|  |  | Rated Impulse withstands voltage i.e. Uimp | ≥ 6.0 kV |
| 2.4 |  | Rated frequency | 50±3% Hz |
| 2.5 |  | Number of Poles | 1 (one), for single phase operation |
| 2.6 |  | Rated continuous current In | 250 Amps/ 200 Amps/ 100 Amps |
| 2.7 |  | Rated ultimate Short circuit Breaking capacity i.e. Icu | 36KA or higher capacity but having operational short circuit breaking facility at 18 kA |
| 2.8 |  | Operating Mechanism | Quick make, quick break type, Manual ON/OFF, automatic and Manual Trip, mechanically trip free, Indicator for “ON-TRIP-OFF” position. Must be equipped with “push to Trip” button in front of Breaker. |
| 2.9 |  | Trip: | Thermal magnetic trip unit. |
|  |  | a) Thermal | Thermal element for overload protection: (0.8-1.2)In. |
|  |  | b) Magnetic | Magnetic element for short circuit protection: (4-10)In. |
| 2.10 |  | Construction | Contacts shall be made of silver alloy bolted terminal for front-wire on entry from top and bottom. The unit shall be weather proof, dust proof and tropicalized, toggle switch for “ON-OFF” operation. Appropriate design grid arc quenchers to make it safe at highest interrupting duty. Main parts of the MCCB must be protected in a molded case to protect this form water. |
| 2.11 |  | Standards | Design, Manufacture, Testing, Installation and Performance shall be in accordance to the latest editions of IEC 60947-1 and IEC 60947-2 or equivalent international standards. |
| 3.0 |  | Enclosure: |  |
| 1. | Each enclosure shall contain one MCCB, be weather tight and be proof against entry of vermin and spiders. The enclosure shall be made of galvanized steel sheet of minimum 2 mm thickness. Provision for 3 mm sheet base to accommodate the breaker and proper sealing arrangement. The enclosure shall be rain, dust and weather proof in accordance to IP 55. The design & material used for the enclosure must be shock proof and fire retardant. The outdoor type enclosure shall be provided with adequate means for outdoor pole mounting and shall be supplied complete with all necessary fitting facilities by clamping or stainless-steel strap & buckles arrangement with poles. The unit shall have slanted roof and rain shed for outdoor type. |  |  |
| 2. | Galvanization shall be as per latest revision of ASTM A90/ BS EN ISO 1461:2009 standard. |  |  |
| 3. | The finish shall suitable for continuous outdoor operation in a tropicalized climate. |  |  |
| 4. | The size of the Enclosure shall be 500mm (Height) x 300mm (Width) x 200mm (Depth). |  |  |
| 5. | The enclosure shall have hinged front door with extra flange and welded eyehole or lug for keeping provision of wire seal/pad locking arrangement. |  |  |
| 6. | The enclosure shall have made of heat resistant insulating material & have facility for grounding. |  |  |
| 7. | The enclosure shall have 8 (eight) mounted glands at the bottom of 32 mm diameter each for cable in and outlet with bushing made of rubber or similar materials. |  |  |
| 8. | Facilities for ventilation must be provided to prevent condensation. |  |  |
| 9. | Necessary fixing channels with adjustable hole including nuts, bolts etc. for mounting the Enclosure on the pole shall be supplied with the Enclosure. |  |  |
| 10. | The front cover of each Enclosure shall have marking “BPDB” and monogram of BPDB and shall also have marking “DANGER” with danger symbol. |  |  |

Features and Accessories

1. 	Terminals shall be completed with bolts and suitable for copper and Aluminium cable for adequate size.

2. 	Suitable manually operated neutral disconnecting link shall be provided for disconnecting the neutral.

3. 	The unit shall be dust proof, weather proof and moisture proof and shall be tropicalized.

4.	Each unit shall be supplied with Constructional and Outline Dimensional drawings, Installation, Operation & Maintenance Manual.

Information Required

The Tenderer/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted along with the tender:

(a)	Manufacturer’s drawing showing outline dimension of the offered MCCB, Enclosure of MCCB and position of the MCCB in the Enclosure and fixing arrangement of the Enclosure on the pole.

(b)	Construction, Installation, Operation & Maintenance Manual.

(c)	Printed catalogue of offered type MCCB describing thermal setting, magnetic settings, interrupting current and other associated data and information.

(d) 	Characteristics curve of offered type MCCB.

(e)	Manufacturer's valid ISO Certificate.

(f)   Manufacturer’s EMC Certificate of Conformity.

(g)  Manufacturer’s EU & CE Certificate conformity.

(h)   Test/Calibration Certificate for the offer type Equipment.

Type Test Reports for offer type similar or higher size MCCB as per relevant Standards in English along with test result from anyone of the following independent testing Laboratory;

a) KEMA, Holland.

b) CESI, Italy,

c) Office of the Gas and Electricity Market, UK/SGS, UK,

d) CPRI, India

e) KERI, South  korea

f) China National Quality Supervision and Testing Center, China.

g) TESTLA ELEKTRİK LABORATUVARLARI TİC. LTD., TURKEY.

The bidder shall also submit the type test reference number and contact person from the independent test laboratory to verify the test report.

25.0 Technical Specifications/Requirements Of Copper Cable (120mm2, 70mm2, 35mm2 & 25mm2)

STANDARDS:

The cable as specified in this Section shall be conforming to the latest edition of the following standards for operation under local ambient conditions. Design, Manufacture, Testing and Performance of the cable shall be in accordance with the IEC 502-1, IEC 60228, BS 6004:1994 or equivalent International standards.

# Specifications:

These single core cables shall be designed as per above standards and suitable for operation at a maximum voltage of 1000V line to line and suitable for use underground buried in earth or in ducts and above ground in air or in buildings under local ambient conditions.

The maximum acceptable length of cable on a drum shall be 500M and shall be supplied on standard non-returnable treated wooden drum, each drum having stencilled on each side: drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

Cable construction shall be as per BS 6004:1994 or equivalent to any internationally acceptable standard. Conductors shall be circular plain annealed copper in accordance with IEC 60228. Thickness of insulation shall be in accordance with IEC 502-1. The over sheath shall be an external layer of black PVC.

A means of identifying the cable size and BPDB ownership shall be inscribed throughout the length of the Cable in a single line on the PVC Insulation. The letters shall be upright block characters embossed on the surface; they are being not more than 300 mm between each group. The manufacturer’s name with year of manufacture and Progressive Meter Marking shall be provided throughout the length of the cable.

Drum wound length of each drum may not vary as tolerance and the sum of total drum length shall be as per ordered quantity. Only one short length of conductor on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerances for the diameter and thickness are acceptable.

| Description | Unit | Requirements |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Cable Size | mm2 | 1CX120 | 1CX70 | 1CX35 | 1CX25 |
| Material |  | PVC Insulated plain annealed copper. | PVC Insulated plain annealed copper. | PVC Insulated plain annealed copper. | PVC Insulated plain annealed copper. |
| Numbers & Diameter of wires | No/mm | 37/2.03 | 19/2.17 | 19/1.53 | 7/2.14 |
| Maximum resistance at 30 °C | /KM | 0.1559 | 0.2723 | 0.524 | 0.727 |
| Nominal thickness of insulation | mm | 1.6 | 1.4 | 1.2 | 1.2 |
| Nominal thickness of sheath | mm | 1.8 | 1.8 | 1.8 | 1.8 |
| Colour of sheath |  | Black | Black | Black | Black |
| Approximate outer diameter | mm | 21 | 17.3 | 13.9 | 12.4 |
| Approximate weight | Kg/KM | 1384 | 858 | 482 | 363 |
| Continuous permissible service voltage | V | 600/1000 | 600/1000 | 600/1000 | 600/1000 |
| Current rating at 30 °C ambient temperature U/G | Amps | 310 | 225 | 155 | 130 |
| Current rating at 35 °C ambient in air | Amps | 350 | 245 | 160 | 125 |

FEATURES AND ACCESSORIES:

  - Conductors shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 120 mm diameter. The interior of the conductor drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Conductor drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate with out undue deterioration.

  - The PVC covering shall be complete with PVC/A for Insulation and PVC-ST2 for Sheath as per requirement of IEC60502-1.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered cable.

b)	Cross-sectional drawings of offered cable.

c)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

d)     Manufacturer's valid ISO 9001 Certificate.

e)    Type Test Reports for PVC insulated and PVC sheathed Copper cable from an independent testing Laboratory/Institute as per relevant Standards (unless otherwise specified).

26.0 Technical Specifications/Requirements Of Duplex Copper Cable (4mm2) & QUADRuplex Copper Cable (6mm2 & 16mm2)

STANDARDS:

The cable as specified in this Section shall be conforming to the latest edition of the following standards for operation under local ambient conditions. Design, Manufacture, Testing and Performance of the cable shall be in accordance with the IEC 502-1, IEC 60228, BS 6004:1994 or equivalent International standards.

# Specifications:

These plain annealed copper conductor for phase, hard drawn copper conductor for neutral, PVC insulated & twisted cables shall be designed as per above standards and suitable for operation at a maximum voltage of 1000V line to line and suitable for use underground buried in earth or in ducts and above ground in air or in buildings under local ambient conditions.

The maximum acceptable length of cable on a drum shall be 1000M and shall be supplied on standard non-returnable treated wooden drum, each drum having stenciled on each side: drum number, code name of conductor, drum wound length together with gross and net weight, the manufacturer name, the purchaser's name and contract number with date. The cover of the drum should be of same treated wood.

Cable construction shall be as per BS 6004:1994 or equivalent to any internationally acceptable standard. Conductors shall be circular plain annealed copper in accordance with IEC 60228. Thickness of insulation shall be in accordance with IEC 502-1.

A means of identifying the cable size and BPDB ownership shall be inscribed throughout the length of the Cable in a single line on the PVC Insulation. The letters shall be upright block characters embossed on the surface; they are being not more than 300 mm between each group. The manufacturer’s name with year of manufacture and Progressive Meter Marking shall be provided throughout the length of the cable.

Drum wound length of each drum may not vary as tolerance and the sum of total drum length shall be as per ordered quantity. Only one short length of conductor on a drum is considered for acceptance, if necessary. For the other requirements, the given data shall be considered as minimum and maximum where necessary. No negative tolerances for the diameter and thickness are acceptable.

| Description | Unit | Requirements for Duplex Cable | Requirements for Quadruplex Cable |  |  |
| --- | --- | --- | --- | --- | --- |
| Cable Size | mm2 | 4rmX4rm | 3X6rm+6rm |  | 3X16rm+16rm |
| Number of Core |  | 2 single Core (Phase+Neutral) | 4 Single Core (3 Phase+ 1 Neutral) |  | 4 Single Core (3 Phase+ 1 Neutral) |
| Material |  | PVC Insulated plain annealed copper. |  |  |  |
| Phase Conductor |  | Plain annealed copper conductor |  |  |  |
| Neutral Conductor |  | Hard drawn copper conductor |  |  |  |
| Insulation Material |  | High quality electric grade weather proof PVC over core for water tightness but ensuring case of stripping |  |  |  |
| Numbers & Nominal Diameter of wires | No/mm | 7/0.85 | 7/1.05 | 7/1.71 |  |
| Maximum resistance at 20 °C | /KM | 4.61 | 3.030 | 1.15 |  |
| Thickness of insulation (Min.) | mm | 1.6 | 1.6 | 1.6 |  |
| Colour of Insulation | - | Phase-Black, Neutral- Green |  |  |  |
| Approximate weight | Kg/KM | 140 | ≥370 | ≥765 |  |
| Continuous permissible service voltage | V | 600/1000 |  |  |  |
| Current rating at 35 °C ambient in air | Amps | 35 | ≥41 | ≥75 |  |

FEATURES AND ACCESSORIES:

  - Cables shall be delivered on standard non-returnable strong wooden drum. The central hole of the drum shall be reinforced to fit on axle size 120 mm diameter. The interior of the conductor drum shall be lined with bituminous paper to prevent the conductor from being in contact with timber or Aluminium water proof paper and felt lining shall overlap at seams by at least 20 mm and the seams shall be sealed.

  - Drum shall be adequately protected by securely fastening substantial wooden battens around the periphery. These battens shall be secured by means of hoop metal bindings. Conductor drum shall be treated in an approved manner to resist termite and fungus attacks and shall be suitable for outside storage for a minimum period of 3 years in an equatorial climate without undue deterioration.

  - The PVC covering shall be complete with PVC/A for Insulation and PVC-ST2 for Sheath as per requirement of IEC60502-1.

  - There shall be only one length of conductor on a drum.

  - Treated wooden drum standard: AWPA C1 – 82, C2 –83, C16 –82, P5 –83.

Information Required:

The Bidder/ Manufacturer as per tender requirements shall provide all information. Besides these, the following information has to be submitted:

a)	Manufacturer’s Printed Catalogue describing specification and technical data for offered cable.

b)	Cross-sectional drawings of offered cable.

c)	Detail weight calculation of the offered cable.

d)	Detail description of testing facilities (Routine & Type Test) at manufacturer's plant.

e)      Manufacturer's valid ISO 9001 Certificate.

TYPE TEST:

Type Test Reports for PVC insulated Duplex & Quadruplex Copper cable from an independent testing Laboratory/Institute as per relevant Standards (unless otherwise specified).

APPROVAL OF DRAWINGS AND SPECIFICATIOS:

Design & Drawing, Specification and Technical Particulars & Guarantees etc, shall be submitted to the Engineer, Director, Design & Inspection–II, BPDB by the Bidder for approval, prior to the manufacturing of the goods. The Bidder shall have to submit 3 (three) sets of the same for Approval within 15 days from the date of signing Contract.

27.  Technical Specifications/Requirements Of 11 KV, 3Cx70 Sq.mm XLPE Cu Cable

The manufacturing process shall be designed to eliminate irregularities like protrusions, voids and contamination etc. to ensure the long-term reliability of the 11kV XLPE Cu cable. The 11kV XLPE Cu cable covered in this specification shall be manufactured by Triple extrusion and Gas curing process ensuring circularity and concentricity of the extruded layers around the conductor and all three layers (conductor screen, XLPE insulation and insulation screen) shall be extruded in simultaneous triple extrusion process. The details of manufacturing process and curing to be adopted shall be mentioned clearly in the offer.

Raw materials used to manufacture the cable shall be of highest quality and it should meet material standards mentioned in IEC 60 502-2.  The materials shall be clean and packed in moisture and dust proof packing.  Material received by manufacturer should be checked/ tested to ensure that it meets material specification.

Loading of the extruder in the manufacturing plant shall be performed entirely closed and dust proof environment.  Contamination shall be avoided by the use of a fully enclosed material handling system.  The use of special means like pressurized air etc. for transport of granules, as far as practicable, shall be avoided.

The cross linking, curing and cooling may be carried out in one operation and shall be a gas curing process under high pressure to eliminate the formation of voids in the insulation and contaminants in the dielectric. Process conditions such as curing and cooling temperatures, production speed etc. shall be closely monitored during manufacture to ensure a good degree of cross-linking through the whole insulation.

The cable will be laid in underground in an area with highly moist soil so metal sheath of either lead or aluminium shall be employed to act as moisture barrier layer.

Cable Construction

The 11kV XLPE Cable shall have stranded compacted round copper conductor, taped with semi conducting tapes, conductor screening with extruded semi conducting thermosetting compound, with completely gas cured XLPE insulation, adequate insulation screening consisting of extruded semi conducting thermosetting compound layer, taped with semi conducting water swellable tape, extruded/welded corrugated Aluminium sheathed and overall extruded termite repellent black PE sheathed with outer conducting layer.

Conductor

The conductor shall be stranded compacted round copper conductor complying the requirement of flexibility Class-2 of IEC 60 228. The wires shall be made of high conductivity copper and shall be stranded mid compacted.  The copper used for the conductor shall be of highest purity. The nominal area of conductor shall be 3X70 sq. mm.

The minimum number of wires in conductor shall be 61 and the maximum DC resistance of conductor shall be 0.268 /KM at 20C.

Conductor Screen

The conductor screen shall consist of an extruded layer of thermosetting semi conducting compound and shall be continuous and cover the whole surface of the conductor.  The screen shall be firmly bonded to XLPE insulation. The minimum thickness of conductor screen shall be 0.8 mm. (approx.)

A non-hygroscopic semi conducting tape may be applied over the conductor surface under extruded layer.  The outer surface of the conductor screen shall be circular and free from irregularities.

Insulation

The insulation shall be cross-linked polyethylene (XLPE).  The insulation material shall comply with the requirement as per IEC 60 502-2. The insulation shall be applied by extrusion and vulcanisation to form a compact homogenous body free from micro voids and contaminants. The nominal thickness of insulation shall be 3.4 mm.

Insulation Screen

The insulation screen shall consist of an extruded layer of thermosetting semi conducting compound and shall be continuous and cover the whole surface area of insulation.  It shall be firmly bonded to the insulation.

The minimum thickness of insulation screen shall be 0.8 mm.

Metallic Screen

The metallic Screen shall consist of a concentric layer of copper wires or a combination of copper wires and helically applied coppertape(s) as per IEC Standard.

The metallic Screen shall be so designed to carry the specified earth fault current of 10KA  for 1 second.

Separation Sheath

The Separation Sheath should covering the whole surface area of the metallic screen as per IEC Standard.

Armour

The armour shall be Aluminium Alloy round wires or Corrugated Aluminum sheath as per IEC Standard.

Outer sheath

The outer sheath shall consist of an extruded layer of black medium density polyethylene. The outer sheath shall be of sufficient hardness to discourage termite attacks.  The properties of outer sheath material shall be as per IEC 60 840. The nominal thickness of outer sheath shall be 2.6mm.

Marking on Outer Sheath

The following particulars shall be either marked on Cable outer sheath or printed over a tape at suitable regular intervals.

- Manufacturer’s name and/or trade name.

- Voltage grade viz. 11 kV

- Cable size (no. of core x conductor cross section).

- Year of manufacture.

- Purchaser’s name i.e. BPDB.

The spacing between one set of marking and lie beginning of the next on the legend shall not exceed 300 mm. In case of printed over a tape, the same shall be provided inside the cable.

Tests for  11kV XLPE  Power Cables .

All type, routine and acceptance (special) tests shall be carried out as per IEC 60 502-2. The manufacturer of cable must have at least ISO 9001 certified quality Assurance system in their manufacturing system.

Routine Tests

The following routine tests shall be carried out on each manufactured length

a)	Partial discharge test

b)	Voltage test

c)	DC voltage test on outer sheath

d)	Conductor resistance test

Special (Acceptance) Tests

The following tests shall be made on samples which, for the tests in items (b) and (g), may be on complete drum length of cable taken to represent batches

a)	Conductor examination

b)	Measurement of electrical resistance of conductor

c)	Measurement of thickness of insulation and non-metallic sheath

d)	Measurement of thickness of metallic sheath

e)	Measurement of overall cable diameter

f)	Hot set test for XLPE insulation

g)	Measurement of capacitance

Frequency of Tests

The above special (acceptance) tests shall be made on one length from each manufacturing series of the same type size of cable, but shall be limited to not more than 10% of the number of lengths in any contract, rounded to upper unity.

Type Tests

The following tests shall be included in the type tests (Electrical) Tests.

a)	Bending test followed by Partial discharge test

b)	Tan  measurement

c)	Heating cycle test followed by partial discharge measurement

d)	Impulse withstand test followed by a power frequency voltage test

Test on cable components

a)	Check for cable construction

b)	Resistivity of semi conducting layers

c)	Test for determining the mechanical properties of insulation before and after ageing

d)	Test for determining the mechanical properties of non-metallic sheath before and after ageing.

e)	Ageing tests on pieces of complete cable to check compatibility of materials

f)	Pressure test at high temperature on sheath

g)	Hot set test on XLPE insulation

h)	Carbon black content of PE sheath

i)	Shrinkage test on XLPE insulation.

- TECHNICAL SPECIFICATION OF 230V, 10(60)A, SINGLE PHASE ENERGY METER.

| Standard | : | The meter shall be designed, constructed and tested in accordance with IEC standard 62052-11,62053-21 or relevant equivalent international standard. |
| --- | --- | --- |
| Installation | : | Outdoor surface mounted |
| Type | : | Electronic. |
| Connection | : | Single phase, two-wire, whole current, Solidly grounded neutral Side Entry Type |
| System Frequency | : | 50 Hz |
| Rated voltage | : | 230 volts |
| Maximum system voltage | : | 250 volts |
| Operating voltage range | : | ± 30% of the rated voltage. |
| Basic current | : | 10 Amps |
| Rated maximum current | : | 60 Amps |
| Power Factor variation | : | 0.5 lag to 0.8 lead |
| Display | : | LCD display |
| Starting current | : | 0.4% of the basic current |
| KWh Register | : | Solid sate LCD display type register. The display shall include- Cumulative Forward KWh Display Register : 5 (five) integral & 1 (one) decimal. Type : Solid state LCD display. |
| Terminal | : | Transparent, Non symmetrical, Side entry type, Front connection and Connection type with extended terminal cover. Minimum 4 (four) Terminals to accommodate 16- sq. millimeter size of cable. The terminal cover of offered type energy meter shall be transparent and can be sealed independently. |
| Accuracy class | : | Class 1.0 |
| Unidirectional | : | Meter must be unidirectional |
| Energy record | : | Meter must be recorded energy even neutral is missing. |
| Meter case | : | The meter shall be constructed by employing flame retardant and high impact strength material. The base, body and frame including terminal block shall be of heat resistive; shock proof and rust proof good quality hard material e.g. unbreakable engineering or stamped metal or molded phenolic resin which shall be capable of withstanding of 145˚C. The base will be provided with 2 (three) screw mounting holes, 1 (one) slotted meter support bracket at the top and 1(one) round hole on each side in the bottom half of the base for securely mounting the meter to the meter board. The meter cover shall be of molded black phenolic resin or alliteratively stamped metal or toughened glass. The meter cover shall be provided with a window of transparent poly-carbonate or toughened glass. |

| Meter Assembly | : | The meter body shall be hermetically sealed or Ultrasonically welded to prevent entrance of moisture, rain and dust into its internal part. |
| --- | --- | --- |
| Service life ( minimum) | : | 15 (Fifteen) years. |
| Battery | : | Each time switch must be provided with lithium battery, which allow the switch to function for a period of not less than 10 (ten) years. The guaranteed life of the battery should not be less than 10 (ten) years. |
| Warranty | : | Minimum 3(Three) years |

##### Technical Feature

- The meter cover shall be provided with Toughened glass/transparent poly carbonate as par IEC standard.

- The meter terminal cover shall be secured to the body with sealable tamper proof screws and transparent.

- Suitable gasket to be attached to the front cover to ensure dust, moisture rain-tight joint and shall be fully waterproof as meter shall be installed in sun and rain (Outdoor type).

- The meter shall have provision for earthling for stamped metal construction.

- The terminal cover shall carry indelibly printed connection diagram attached inside.

- The meter shall be supplied in factory calibrated and sealed condition along with copy of routine test certificates.

- The meter shall have nameplate distinctly and indelibly marked with the following in addition to all standard information.

- '' With insignia of the Organization''

- Manufacturer's name and country.

- Year of manufacture.

- Model No.

- Voltage and current rating (basic current and maximum current)

- Frequency

- Accuracy class

- Meter serial number

- Meter Constant (Impulse per KWh)

- Type test report of all tests as per relevant standard in English along with test results of the offered type energy meter from any of the internationally recognized independent test laboratory.

##### 29.0 TECHNICAL SPECIFICATIONS & REQUIREMENTS OF 110V, 3X5(6)A, 3-PHASE, 4-WIRE ACCURACY CLASS 0.2S SOLID STATE DOUBLE TARIFF PROGRAMMABLE ENERGY METER WITH MODEM.

The meters are required for the purpose of energy metering of 230/132/33/11 kV line Utility Billing Metering through CT & PT, KWh is the unit for revenue purpose.

| System voltage | : | Nominal service voltage 110V, 3 phase 4 wire, solidly grounded neutral at source end , maximum system voltage 120V line to line. |
| --- | --- | --- |
| System frequency | : | 50±2 Hz |
| Standard | : | The Energy Meter should be designed, manufactured and tested in accordance with IEC 62052-11, 62053-22, 62053-23 and IEC 61850 or equivalent converter specified in this specification |
| Installation | : | Indoor/Outdoor installation |
| Type | : | Solid State (Static) |
| Protection Class | : | IP53 |
| Application | : | Registration of KWh (Cumulative Peak, Off-Peak & Total), Total Cumulative KVarh (Q1+Q4) or programmable, KW on 3- phase, 4-wire supply for balanced &unbalanced load (default unidirectional) and bidirectional can be customized). TOU will be programmable. Default Peak 17:00-23:00 hrs. & Off-Peak rest of the day as per Bangladesh Standard Time (BST). Minimum six Tariffs should be customizable. |
| Connection | : | 3-phase 4-wire, solidly grounded neutral system. |
| Nos. of element | : | 3 (Three) |
| Rated current | : | Basic current 5 amps and maximum current within 6 Amps. |
| Register & Display | : | Solid state LCD display type register. The display Register shall be programmable, automatic scrolling which typically include: |
|  |  | - Meter ID - Time & date - Cumulative KWh (Total, Peak & Off-Peak) - Cumulative Total KVarh (Q1+Q2) /(Q3+Q4)/ (Q1+Q4) - Export & Import (Kwh, Kvarh& MD) - Maximum demand (KW) with time & date. Maximum demand (MD) in kW shall be registered using the technique of cumulating on integration period controlled by built-in process and the MD shall be continuously recorded and the highest shall be indicated. - Cumulative Maximum demand (kW) for billing month. The highest MD shall be added to the cumulative store, which shall be automatically initiated after an interval of one month / one billing period by means of built-in timing device. - Cumulative Number of MD reset (Automatic& manually). - Average PF for billing period. Instantaneous : - Phase Voltage with indication - Phase Amps. - Power factor (average). - System Demand (KW) - Voltage angel (each phase) - Current angle(each phase) - Tampering indication in the display (Latched). - Power Flow co-ordinate/Sign of power flow direction in the display both for Kw &Kvar. |
| Memory storage | : | The meter shall have sufficient capacity (minimum 1MB) to store the following readings and data in non-volatile memory even in case of power failure. - Number of power interruption with date & time (min. 500 events). - Inclusion of events and Temper items are programmable typical items are Power Failure, Demand Reset, Time Change, History Log, Operator Code, Terminal Cover open, Front Cover Open etc. The event & Tamper log should be recorded with date and time in separate memory . - Current & Previous (Min.12 ) months registered Cumulative KWh (Peak, Off-Peak & Total), Total Cumulative KVarh (Q1+Q4), MD, Cumulative MD, Billing PF etc. ie Billing History. Export & Import (Kwh, Kvarh& MD). The stored data could not be deleted/edit, only read only mode shall be accepted. - Total Nos. of Demand reset with date & time. - Load Profile data at 30 minutes interval [ kWh Del, Kwh Rec., Kvarh Del, Kvarh Rec., Phase wise Voltage & Current, Power Factor (customize).Instantaneous Values for voltage & Current and Average values for Kwh&KVarh. - Integration period : 30 (thirty) minutes. The meter must have sufficient capacity to store data at 30 (thirty) minutes interval for at least 12(Twelve) Months with 14 channel data recording. |
| Security Access | : | Equipment Identification Codes, Access Code & Security Code. |
| Accuracy class | : | Accuracy class is 0.2S |
| Number of digit |  | Minimum 5 (Five) integer and 3 (Three) decimal (configurable). |
| Time switch | : | The time switch shall be built-in solid state type and shall be designed to perform a load cycle of operation. Time switch shall operate in between Peak & Off-peak as per predefined time zone (programmable). The maximum error shall be kept within 1 (one) second per day. Time error should be adjustable with clock time. |
| Battery reserve | : | Each Meter must be provided with lithium battery which allow the meter to function for a period of the guaranteed life of the battery should not be less than 15 (fifteen) years. Min self-life shall be 5 (Five) years. Have provision for easy replacement of battery. Battery should support biasing for Internal Clock, Minimum three times reading display during power failure with max 8 hours power interruption. In addition a super cap to provide(internally)to maintain clock power during battery replacement. |
| Construction | : | The meter cover shall be made of polycarbonate/acrylic /phenolic /resin. The meter cover &base plate shall be provided with security sealing provisions to prevent unauthorized access to the internal meter works and base plate sealing shall be designed to accommodate both padlock and wire type seal. IEC meters shall be minimum IP53. It shall be designed to operate continuously for the normal life of the meter in unsheltered outdoor tropical location exposed to the elements without corrosion or other damage to parts to adversely affect meter accuracy or reliability. |
| Terminal | : | Minimum 10 Terminals to accommodate up to 06 sq. mm size of cable. Bottom entry, front connection with sealing provision. Meter shall have extended terminal to accommodate communication module. There shall be free space between bottom of the terminal and the bottom of the terminal cover. |
| Service life of meter | : | Shall be minimum 15 (fifteen) years. |
| Visual indication of operation | : | Pulse indicator on the front of meter as per meter constant. Should be in Red color as per factory default value. |
| Special condition | : | - The factory calibration conforms to relevant IEC or equivalent international standard. LCD display shall be as programmed consecutively and continuously one after another. The display shall be automated i.e. no external means shall be required to see the display. Each display shall last for at least 5 (five) sec (Programmable). In addition to normal display there should be an alternate mode of display where display items are also programmable and will be activated by pressing a switch. The system will return to normal mode if the said switch is not pressed for 10 Min(Programmable delay time). - Meter Electronic Circuit biasing voltage shall have any phase biased both of phase-phase and phase-neutral minimum basing voltage 40V. |
| Meter Sealing | : | The Energy meter body will be hermetically sealed/ultrasonically welded with mechanically interlocked to avoid unauthorized opening of meter cover. Hermetically sealed/ Ultrasonic welded/ mechanically interlocked sealed means break to open. Another sealing provision is required for hardware lock system (micro switch) to configure meter parameters. Otherwise the bid will be rejected. |
| Communication port | : | The meter must be provided with a suitable communication port to allow downloading of desired information stored in the meter through an optical port of relevant standard to PC. In addition the meter shall be equipped with remote GSM, GPRS & PSTN communication option so that BPDB can go for AMR Communication with the meter. |
| Remote Communication | : | The meter shall be equipped with external Plug & Play 4G communication module. Antenna with minimum 3.0 meter extension cable with all necessary accessories need to be provided. The meter including modem shall be compatible with existing AMR system of BPDB. |
| Software Feature Software Valid Licensing & Training Requirement | : : | The meter shall have the following features in software: - The whole software should be operative/ compatible in windows operating system. - The software must be able to display and download of recorded & instantaneous data from meter are Programmer ID, Meter ID, Kwh (Peak, Off-Peak, Total, Export, Import), Kvarh, KW, KVar, PF, Per phase Voltage, Per phase current, Phase voltage angle, phase current angle, Load profile minimum 8(eight) channels Event & Temper log etc. - Software should be able to display instantaneous vector diagram/Vector at the time of download. - Parameterization software shall be provided for configuration of the meter as per BPDB standard. Both the software meter should have access code (min 3 access level) allocated. Tender shall be submitted Software valid license. Optional Provision for local training by the tenderer. |

TAMPER AND FRAUD PROTECTION FEATURE:

The meter shall have the following features to prevent/detect tamper and fraud:

- Phase Sequence Reversal: The meter should work accurately irrespective of phase sequence of supply.

- Missing Potentials: The meter shall be capable of detection occurrence of missing potential with a LCD indication in display, which can happen due to intentional/accidental disconnection of potential link(s).

- Terminal cover must have micro-switch provision to be included tamper detection with a latchable   indication  in LCD.

SOFTWARE ACCESS :

- Software Access : Both the Software and Meter should have access code(min. 3 access level) at different access level  for the operation of software & meters. The meters shall not have provision for configuration by software only, i.e.  For meter configuration both software lock and hardware lock shall have to be opened otherwise no one can configure the meters. Hardware lock shall consist with a micro switch which must be under sealing provision.

OTHER TECHNICAL FEATURES:

- The base cover or socket shall be provided security sealing provisions.

- The meter shall be provided with engraved/ permanently printed connection diagram.

- The meter with metallic socket shall have provision of earthing.

- The meter and meter accessories, enclosure should be the same country of origin.

- Auxiliary biasing should have alternate provision of energizing in case of PT failure.

- The meters shall have Total Harmonics Distortion (THD) counting provision

- The meters should have loss compensation input provision due to CT, PT error

- Software should be able to display instantaneous vector diagram at the time of down load.

- The meter shall have permanently printed nameplate distinctly marked with the following in addition to all standard data :

- Serial number.

- Meter Type

- Voltage and current rating.

- Accuracy class.

- Frequency.

- Meter constant.

- Number of wire.

- Year of manufacture.

- Name of manufacturer.

- The word “BPDB” and Logo of BPDB.

Display of measured values/ Meter Display

- The Sequence of LCD display should be factory default with a provision of user programmable.

- The contrast setting of LCD display should be visible in different lighting environment and distinctly visible in broad daylight.

- The meter should be capable of displaying time and date, the direction of energy i.e. as import/export or +/-, active tariff, and internal fault indicators.

- The meter shall have provision of auto scrolling during absence of power with internal lithium battery backup for at least 6(six) hours.

- In addition, alternate mode of display will be activated by pressing a switch. In the same way if the said switch is not pressed for ....sec (programmable) it will return to normal mode.

- Missing of PT or any phase(L1, L2, L3)

- The four-quadrant diagram (Vector Group) display

Meter Parameterization Software:

- Meter must have a factory default pre-defined parameterization software to display the features automatically as described before. For TOU 17:00-23:00 to be considered as Peak and rest of the time will be considered as Off-Peak as per BST.

Event Log:

- The meter shall record the following events with time and date not less than 500 nos. as follows:

Power failure (On/Off) with time and date, log in/log out with user ID, Time of Use (TOU) reset time and date change, terminal cover open, front cover open, tamper, PT/CT failure, demand reset, any faults etc. Event log storage provision during configuration done in all cases are needed. These events record will be additional to the meter default event recording system. Only log in/log out event shall have provision for acknowledgement to the designated person via SMS service.

EXTERNAL MODEM WITH ACCESSORIES

GSM/GPRS modem with RS-232 & RS-485 ports, meter interfaced power supply, connection cables, antenna with minimum 3.0 meters cable, mounting facilities, enclosure (if necessary). The modems will be capable of GSM and GPRS connectivity simultaneously. For GSM configuration the AT command will be available and for GPRS communication the APN, reset time, username, password, port number, etc. are configurable. The modem will have the following specification. The meter shall be compatible with BPDB AMR (Automated Meter Reading) provision.

Interruption (< 1 ms), RS-232 (at least 1), GPRS class 10, operating band 900/1800, auto reset capability (with phone call, SMS). The modem will be robust, durable and compatible with the employers existing service condition. The modem should be offer able from meter bias power, no external source is required.

Optical communication probe (Min 5 Nos.) for download data from meter shall be provided.

List of eligible Meter Manufacturers and country of manufacture for this Tender

a) European Country.

b) North American Country.

c) Japan

d) Australia

The tenderer should submit authentic document with the tender against the country and location of the

offered electric Energy Meter Manufacturing plant which will be verified during tender evelauation.

Tests at Manufacturers works

General

Functional electrical, material, mechanical and hydraulic tests shall be carried out at manufacturers’ premises. The extent and method of recording the results shall be agreed by the Purchaser in sample time to enable the tests to be satisfactorily witnessed or to make any changes to the proposed program of tests.

Material Tests

The supplier shall provide test pieces free of charge as required to enable the quality of the material to be determined at the supplier’s expense. Purchaser may at its own discretion and by specific arrangement accept certified particulars of tests carried out in the absence of his authorized representative.

Type Test

Type tests are required to prove the general design of the offered equipment’s/ materials. The Tenderer shall submit the type test reports of the offered equipment’s/ materials from

a)	KEMA, Holland.

b)	UL International New Zealand/Parkside Laboratories, New Zealand.

c)	South African Bureau of Standards (SABS).

d)	MET Laboratories Inc., USA

e)	 Office of the Gas and Electricity Market, UK /SGS, UK

f)	 European Measuring Instruments Directive (MID) recognized labs.

g)	CESI, Italy.

h)	Essef, France

i)	CPRI, India.

Type Test shall be authenticated by Purchaser during tender evaluation stage. Test organization/Laboratory shall reply/confirm the type test report, it’s genuinity otherwise tender shall be non-responsive. It is responsibility of the Tenderer to facilitate the authentication.

Routine Tests

All equipment’s/ materials shall be subjected to routine tests as per latest version of relevant IEC or equivalent international standards as mentioned in the contract at the manufacturers works and shall include, but not be limited to, an operational test.

Battery Test Report

Manufacturer’s submitted Battery Test Report from recognized lab.

Test shall be authenticated by Purchaser during tender evaluation stage. Test organization/Laboratory  shall reply/confirm the type test report, it’s genuinity.

30.  TECHNICAL SPECIFICATIONS & REQUIREMENTS OF 400V, 3X10(60) A, 3-PHASE, 4-WIRE SOLID STATE DOUBLE TARIFF FULLY PROGRAMMABLE ENERGY METER.

The meters are required for the purpose of energy metering of consumer who purchases power at 400 volt line.  kWh is the unit for revenue purpose.

| System voltage | : | Nominal service voltage 400V, 3 phase 4 wire, solidly grounded neutral at source end, maximum system voltage 440V line to line. |
| --- | --- | --- |
| System frequency | : | 50±2 Hz |
| Standard | : | The Energy Meter should be designed, manufactured and tested in accordance with IEC 62052-11, 62053-21 and 62053-23 or ANSI C 12.16, 12.10 (latest publication) or specified in this specification |
| Installation | : | Indoor/Outdoor installation |
| Protection Class | : | IP53 |
| Type | : | Solid state (Non Rotating/Static). |
| Application | : | Registration of KWh (Cumulative Peak, Off-Peak & Total), Total Cumulative KVarh (Q1+Q4), KW on 3- phase, 4-wire supply for balanced & unbalanced load (by default unidirectional and bidirectional /can be customized). TOU will be programmable. Default Peak 17:00-23:00 hrs. & Off-Peak rest of the day as per Bangladesh Standard Time (BST). Minimum four Tariffs should be customizable. |
| Connection | : | 3-phase 4-wire, solidly grounded neutral. |
| Nos. of element | : | 3 (Three) |
| Rated current | : | Basic current 10 amps and maximum current 100 amps (As per PG4-4). |
| Register & Display | : | Solid state LCD display type register. The display Register shall be programmable, automatic scrolling which typically include : |
|  |  | - Meter ID - Time & date - Cumulative KWh (Peak , Off-Peak & Total) - Cumulative Total KVarh (Q1+Q4) - Maximum demand (KW) with time & date. Maximum demand (MD) in kW shall be registered using the technique of cumulating on integration period controlled by built-in process and the MD shall be continuously recorded and the highest shall be indicated. - Cumulative Maximum demand (kW) for billing month. The highest MD shall be added to the cumulative store, which shall be automatically initiated after an interval of one month / one billing period by means of built-in timing device. - Total Number of MD reset (Automatic & manually). - Average PF (Power Factor) for billing period. - Features shall be programmable Instantaneous : - Phase Voltage with indication - Phase Amps with indication. - Power factor (average). - System Demand (KW) - Voltage angel (each phase) - Current angle(each phase) - Tampering indication in the display (Latched). - Power Flow co-ordinate/Sign of power flow direction in the display. |
| Memory storage | : | The meter shall have sufficient capacity (minimum 512 KB) to store the following readings and data in non-volatile memory even in case of power failure. - Number of Power Interruption with date & time (minimum 500 events). - Event logs with operator code & Tempering items with date & Time (Power Failure, Demand Reset, Time change, Terminal cover open, Body cover open etc.) - Billing history: Current & Previous minimum 12 months Cumulative Kwh (Peak, Off-Peak & Total), Total Kvarh (Q1+Q4). MD with date & time. - Current & Previous month registered with max. KW demand since last MD reset with date & time of its occurrence. - Total Number of Demand reset. - The Meter must have sufficient capacity to store data at 30 (Thirty) minutes interval for at least 120 (one hundred Twenty ) days with min.14 channels data. - Load profile data. - Phase Voltage. - Phase Current. - PF - Features shall be programmable. |
| Security Access | : | Equipment Identification Codes, Access Code & Security Code. |
| Accuracy class | : | Accuracy class is 1.0 (One) |
| Number of digit |  | Minimum 6 (Six) integer with 1 (One) decimal (Total 7 digit). |
| Time switch | : | The time switch shall be built-in solid state type and shall be designed to perform a load cycle of operation. Time switch shall operate in between Peak & Off-peak as per predefined time as mentioned. The maximum error shall be kept within 1 (one) second per day. Time error adjustment facility shall be provided. |
| Battery reserve | : | Each Meter must be provided with internally rechargeable lithium battery which allow the meter to function for a period of the guaranteed life of the battery should not be less than 15 (fifteen) years both for operating & shelves life and shall have provision for easy replacement. power failure & continuous bias power for meter check. In addition a super cap to provide (internally) to maintain clock power during battery change. |
| Construction | : | The meter shall be completely self-contain round socket or base connected type. The meter cover shall be made of polycarbonate/acrylic /phenolic /resin and socket cover shall be made of metal. The meter cover and socket /base plate shall be provided with security sealing provisions to prevent unauthorized access to the internal meter works and socket / base plate sealing shall be designed to accommodate both padlock and wire type seal. IEC meters shall be minimum IP53. The ANSI Standard meter shall be effectively sealed to prevent entrance of rain and dust into its internal parts. The meter shall pass Rain test described in underwriter’s laboratory standard UL-50 (USA) for type 3 enclosures. A general purpose finish of class 1 as specified in section 7 of ANSI C12.10 shall be provided for the meter and it shall meet the requirement of weather simulation test (Sec. 7.2.1 of ANSI C12.10) and salt spray test (ASTM B117). It shall be designed to operate continuously for the normal life of the meter in unsheltered indoor/outdoor tropical location exposed to the elements without corrosion or other damage to parts to adversely affect meter accuracy or reliability. |
| Enclosure for IEC Standard Meter | : | The meter shall be surface mounted in an indoor/outdoor wall mounted metering enclosure box with necessary wiring. The enclosure box should be made either of high quality flame retardant ABS Resin of minimum 3 mm thickness or of galvanized sheet steel of minimum 1.22 mm (18 SWG) thickness or of auto extinguishable, shockproof and UV resistant, hot molded glass reinforced polyester of minimum 3 mm thickness. The box shall have hinged front door with one toughened glass window to enable easy reading of meter. The metering box shall be weather proof, dust proof, rodent and inspect proof in accordance with enclosure classification IP53. Service cable entry and exit will be bottom/sides of the box and 40 (forty) mm diameter X 2 Nos. of hole with black PVC conic cable gland shall be provided for entry & exit for this purpose All material parts shall have anti-corrosive protection. All materials shall be designed, manufactured and tested as per IEC or equivalent International standards except as mentioned. The front door shall have sealing provision in the closed position. |
| Socket for ANSI Standard Meters | : | Meter sockets shall be suitable for installation of offered type meter. Meter sockets shall be 3-phase, 4-wire, 600 volt class, made from 16 gauge sheet metal. Meter sockets shall be similar except as described below. Meter sockets shall approximately 14 (35.6 cm) H9(22.9cm) W4 (10.2 cm) D and rectangular in shape. Sockets shall be ring less type, sealing latch to be stainless steel and have adequate means for socket grounding. Meter socket shall have 2 knockouts with a range up to 2(5 cm) Diameter, all the bottom. Meter socket shall comply with ANSI C 12.6, 12.10 The Socket shall have self adhesive printed “connection diagram” distinctly marked in addition to all standard data. |
| Terminal | : | Socket connected, bottom entry type, front connection, and connection type with extended terminal cover: Minimum 08 (Eight) Terminals to accommodate up to 16 sq. mm size of cable. The terminal cover for the offered energy meter shall be extended type, and which can be sealed independently. There shall be free space between bottom of the terminal and the bottom of the terminal cover. |
| Service life of meter | : | Shall be minimum 15 (fifteen) years. |
| Visual indication of operation | : | Pulse indicator on the front of meter as per meter constant. Should be in Red color as per factory default value. |
| Special condition | : | - The factory calibration conforms to relevant IEC or equivalent international standard. LCD display shall be as programmed consecutively and continuously one after another. The display shall be automated i.e. no external means shall be required to see the display. Each display shall last for at least 5 (five) sec. In addition to normal display there should be an alternate mode of display where display items are also programmable and will be activated by pressing a switch. The system will return to normal mode if the said switch is not pressed for......sec (programmable). - Meter Electronic Circuit biasing voltage shall have any phase biased both of phase-phase and phase-neutral minimum basing voltage 80V. |
| Meter Sealing | : | The Energy meter body will be hermetically sealed or ultrasonically welded or mechanicaly interlocked to avoid unauthorized opening of meter cover. Hermetically sealed means break to open. Otherwise the bid will be rejected. |
| Communication Port | : | The meter must be provided with a suitable communication port to allow downloading of desired information stored in the meter through a optical port of relevant standard to PC. In addition the meter shall have equipped with RS232/RS485 port so that BPDB can go for AMR communication with the meter in future. |

SOFTWARE FEATURE:

The meter shall have the following features in software:

- The whole software should be operative/ compatible in windows operating system.

- The software must be able to display and download  of recorded & instantaneous data from meter are Programmer ID, Meter ID, Kwh (Peak, Off-Peak, Total, Export, Import), Kvarh, KW, KVar, PF, Per phase Voltage, Per phase current, Phase voltage angle, phase current angle, Load profile minimum 8(eight) channels Event & Temper log etc.

- Software should be able to display instantaneous vector diagram/Vector at the time of download.

- Both the software meter should have access code (min 3 access level) allocated to a person by the administrator at different access level for the operation of software and meter.

TAMPER AND FRAUD PROTECTION FEATURE:

The meter shall have the following features to prevent/detect tamper and fraud:

- Phase Sequence Reversal: The meter should work accurately irrespective of phase sequence of supply.

- Missing Potentials: The meter shall be capable of detection occurrence of missing potential with indication in LCD display, which can happen due to intentional/accidental disconnection of potential link(s).

- Terminal cover must have micro-switch provision to monitor unauthorized opening. Opening of terminal cover shall trigger an event to be recorded in the event log memory.

TECHNICAL FEATURE

- The meter base cover and socket / enclosure shall be provided security sealing provisions to prevent unauthorized access to the internal meter works.

- The meter shall be provided with connection diagram.

- The meter and socket/enclosure shall have provision of earthing.

- Meter must operate and accurately register demand and energy when service voltage is applied across any two of the three input terminals or when service voltage is applied from any input terminal to neutral. Meter will continue to operate even the neutral is missing.

- The meter and socket/enclosure must be the same country of origin other wise the bid will be rejected.

- The registration of KWh (Peak & off-peak) on 3-phase, 4-wire supply for balanced & unbalanced load will be unidirectional. i.e. if one, two or  three phase supply is/are reversed, it will take the absolute (kWh-del) + absolute (kWh-rev) and will add them together as total 3-phase KWh.

- The meter shall have permanently printed nameplate  distinctly marked with the following in addition to all standard data :

- Serial number.

- Meter Type

- Voltage and current rating.

- Accuracy class.

- Frequency.

- Meter constant.

- Number of element, number of wire and multiplication factor (if any).

- Year of manufacture.

- Name of manufacturer.

- The word “BPDB” and insignia of BPDB.

Display of measured values/ Meter Display:

- The sequence of LCD should be user programmable.

- The contrast setting of LCD display should be visible in different lighting environment and distinctly visible in broad daylight.

- The meter should be capable of displaying time and date, the direction of energy i.e. as import/export or +/-, active tariff and internal fault indicators.

- The meter shall have provision of auto scrolling during absence of power with internal lithium battery backup for at least 6(six) hours.

- In addition alternate mode of display will be activated by pressing a switch. In the same way if the said switch is not pressed for ....sec (programmable) it will return to normal mode.

Meter Parameterization Software:

- Meter must have a factory default pre defined parameterization software to display the features automatically as described before. For TOU 17:00-23:00 to be considered as Peak and rest of the time will be considered as Off-Peak as per BST.

31.   Tests at Manufacturers works

General

Functional electrical, material, mechanical and hydraulic tests shall be carried out at manufacturers’ premises. The extent and method of recording the results shall be agreed by the Purchaser in ample time to enable the tests to be satisfactorily witnessed or to make any changes to the proposed program of tests.

Material Tests

The supplier shall provide test pieces free of charge as required to enable the quality of the material to be determined at the supplier’s expense. Purchaser may at its own discretion and by specific arrangement accept certified particulars of tests carried out in the absence of his authorized representative.

Type Test

Type tests are required to prove the general design of the offered equipments/ materials. The Tenderer shall submit the type test reports of the offered equipments/ materials from internationally reputed independent testing laboratory as per latest version of relevant ANSI/ IEC or equivalent international standards as mentioned in the contract.

Routine Tests

All equipments/ materials shall be subjected to routine tests as per latest version of relevant ANSI/ IEC or equivalent international standards as mentioned in the contract at the manufacturers works and shall include, but not be limited to, an operational test.

- End Mile Connection

#### General

The Contractor shall be responsible for an end mile connection i.e the endpoint appears to extend up to the metering connection of the end users, i.e., the residential units.;. This section of the document includes the design, manufacture, testing & inspection, supply of end mile connection as specified.

#### Scope of Supply

- The end mile connection shall comprise with the following material:

| SL No | Item |
| --- | --- |
| 1 | Single Phase Meter |
| 2 | Three Phase Meter |
| 3 | 4RM Duplex Copper Cable |
| 4 | 6RM Duplex Copper Cable |
| 5 | MCCB with Box |
| 6 | Connector & other accessories |

#### Codes and Standards

The equipment specified in this Section shall conform to the latest edition of the appropriate IEC specifications and other recognized international standard. In particular:

- IEC 	62052-11 Electricity metering equipment (AC) – General requirements, tests and test conditions – Part 11: Metering equipment

- IEC 62053-21 Electricity metering equipment - Particular requirements - Part 21: Static meters for AC active energy (classes 0,5, 1 and 2)

- IEC 62053-23 Electricity metering equipment - Particular requirements - Part 23: Static meters for reactive energy (classes 2 and 3)

- IEC 60502-1 Power cables with extruded insulation and their accessories for rated voltages from 1 kV (Um = 1,2 kV) up to 30 kV (Um = 36 kV) - Part 1: Cables for rated voltages of 1 kV (Um = 1,2 kV) and 3 kV (Um = 3,6 kV)

- IEC 60228 Conductors of insulated cables

- BS 6004:1995 Specification for PVC-insulated cables (non-armoured) for electric power and lighting

#### Single Phase Meter

The characteristics/features of Single-Phase Meter shall be as follows:

1. The meter cover shall be provided with Toughened glass/transparent poly carbonate as par IEC standard.

2. The meter terminal cover shall be secured to the body with sealable tamper proof screws and transparent.

3. Suitable gasket to be attached to the front cover to ensure dust, moisture rain-tight joint and shall be fully waterproof as meter shall be installed in sun and rain (Outdoor type).

4. The meter shall have provision for earthling for stamped metal construction.

5. The terminal cover shall carry indelibly printed connection diagram attached inside.

6. The meter shall be supplied in factory calibrated and sealed condition along with copy of routine test certificates.

7. The meter shall have nameplate distinctly and indelibly marked with the following in addition to all standard information.

a) '' With insignia of the Organization''

b) Manufacturer's name and country.

c) Year of manufacture.

d) Model No.

e) Voltage and current rating (basic current and maximum current)

f) Frequency

g) Accuracy class

h) Meter serial number

i) Meter Constant (Impulse per KWh)

8. Type test report of all tests as per relevant standard in English along with test results of the offered type energy meter from any of the internationally recognized independent test laboratory.

#### Three Phase Meter

The characteristics/features of Three Phase Meter shall be as follows:

| Installation | : | Outdoor installation. |
| --- | --- | --- |
| Type | : | Solid state. |
| Application | : | Registration of KWh (Peak & off-peak), Total KVarh (Q1+Q4), KW on 3-phase, 4-wire supply for balanced & unbalanced load (unidirectional). Peak 17.00-23.00. hrs and off peak 23.00-17.00 hrs Bangladesh standard time. The software shall be compatible with Windows operating system. |
| Connection | : | 3-phase 4-wire solidly grounded neutral. |
| Nos. of element | : | 3 (Three) |
| Rated current | : | Basic current 10 amps and maximum current 100 amps. |
| Register | : | Solid state LCD displays type register. The display shall include: |
|  |  | - Meter ID - Time & date - Cumulative KWh (Peak & off-peak) - Cumulative Total KVarh (Q1+Q4) - Maximum demand (KW) with time & date - Cumulative Maximum demand (kW) for billing month. Maximum demand (MD) in kW shall be registered using the technique of cumulating on integration period controlled by built-in process and the MD shall be continuously recorded and the highest shall be indicated. The highest MD shall be added to the cumulative store, which shall be automatically initiated after an interval of one month / one billing period by means of built-in timing device. - Integration period: 30 (thirty) minutes. - Number of MD reset (Automatic& manually). - Average PF (Power Factor) for billing period. Instantaneous: - Phase voltage with indication - Phase amps with direction. - Power factor (average). or P.F. Angle(each phase) Demand (KW) - Voltage angle (each phase) - Current angle (each phase) - Tampering indication in the register. |
| Memory storage | : | The meter shall have sufficient capacity (minimum 95 KB) to store the following readings and data in non-volatile memory even in case of power failure. - Equipment identification codes, security codes and access codes. - Number of power interruption with date & time (minimum 100 events). - Latest power failure: time & date. - Date & time of meter tempering (Voltage & current missing, Demand reset, time change). - Event logs (Power failure, Demand reset, Time change, History log) - Current & Previous month registered in KWh (Peak & off-peak), Total KVarh (Q1+Q4). - Current & Previous month registered with maximum KW demand since last MD reset with time and date of its occurrence. - Nos. of Demand reset. The meter must have sufficient capacity to store data at 30 (thirty) minutes interval for at least 90 (ninety) days. - Load Profile data ( kWh, KVarh (Q1+Q4)) - Phase voltage or Vh - Phase amps or Ah |
| Accuracy class | : | Accuracy class shall not exceed 1.0 (0ne) |
| Number of digit | : | Minimum 5 (five) integer with 1 (One) decimal (Total 6 digit). |
| Type of display | : | Solid-state LCD display. |
| Time switch | : | The time switch shall be built-in type and shall be designed to perform a present cycle of operation. Time switch shall reset MDI at the end of every month (billing period) automatically. In the event of failure of power supply and battery, at the same time set memory shall not be lost i.e. the set program shall be recorded in non-volatile memory. The maximum error shall be kept within  1 (one) second per day. Time error adjustment facility shall be provided. |
| Battery reserve | : | Each time switch must be provided with lithium battery, which allow the switch to function for a period of not less than 10 (ten) years. The guaranteed life of the battery should not be less than 10 (ten) years and shall have provision for easy replacement by the purchaser. The shelf life of the battery should be minimum 15(fifteen) years or more. |
| Construction | : | The meter shall be completely self-contain round socket or enclosure type. The meter cover shall be made of polycarbonate/acrylic /phenolic /resin and socket/enclosure cover shall be made of metal polycarbonate/ acrylic /phenolic /resin. The meter cover and socket /enclosure cover shall be provided with security sealing provisions to prevent unauthorized access to the internal meter works and socket/enclosure cover sealing shall be designed to accommodate both padlock and wire type seal. |
| Terminal | : | Socket connected type/Non-symmetrical, bottom entry, front connection, and connection type with extended terminal cover: Minimum 07 Terminals to accommodate up to 16 sq. mm size of cable. The terminal cover for the offered energy meter shall be extended type, and which can be sealed independently. There shall be free space between bottom of the terminal and the bottom of the terminal cover. |
| Connection | : | 3-phase, 4-wire solidly grounded neutral. |
| Service life of meter | : | Shall be minimum 15 (fifteen) years. |
| Visual indication of operation | : | Pulse indicator on the front of meter as per meter constant and be programmable |
| Meter Sealing | : | The Energy meter body will be hermetically sealed or ultrasonically welded or Cover Bonding Sealed/ Fusion welded to avoid unauthorized opening of meter cover. |

#### 4RM/6RM Duplex Copper Cable

The characteristics/features of 4RM/6RM Duplex Copper Cable shall be as follows:

| Description | Unit | Requirements |  |
| --- | --- | --- | --- |
| Cable Size | mm2 | 4rmX4rm | 6rmX6rm |
| Material |  | PVC Insulated plain annealed copper. |  |
| Phase Conductor |  | Plain annealed copper conductor |  |
| Neutral Conductor |  | Hard drawn copper conductor |  |
| Insulation Material |  | High quality electric grade weather proof PVC over core for water tightness but ensuring case of stripping |  |
| Numbers & Nominal Diameter of wires | No/mm | 7/0.85 | 7/1.05 |
| Maximum resistance at 20 °C | /KM | 4.61 | 3.08 |
| Thickness of insulation (Min.) | mm | 1.6 | 1.6 |
| Colour of Insulation | - | Phase-Black, Neutral- Green |  |
| Approximate weight | Kg/KM | 140 | 186 |
| Continuous permissible service voltage | V | 600/1000 |  |
| Current rating at 35 °C ambient in air | Amps | 35 | 45 |

#### Tests

- A comprehensive FAT has to be conducted and witnessed by the Employer/Employer’s Engineer and the Contractor. The Contractor shall carry the costs for all testing. Prior to the tests 30 days, a test procedure shall be submitted to the Employer/Employer’s Engineer for the approval. A full protocol and test results shall be submitted to the Employer’s Engineer after the testing.

#### Guarantee

- The Supplier shall guarantee all characteristic required. The Supplier shall present and supervise all the guarantee tests.

- The Supplier shall guarantee that the supplied equipment, material, or part thereof shall follow the specifications hereto and shall be unused products, free from any defects in design, material or workmanship. Spare parts furnished shall be identical or equivalent to original parts (spare parts are quoted as optional).

- The warranty period must be two (2) years and it shall begin from the Operational acceptance. This warranty implies that the Supplier and the Contractor shall repair, or replace, if necessary, all the elements damaged during this period.

- This warranty implies that the Supplier shall repair, or replace, if necessary, all the elements damaged during this period.

#### Documentation

- The Contractor shall provide as minimum the following documentation, included in the Bid documents:

- Equipment list for End mile connection

- Technical Data Sheet for each equipment

- Voltage Drop Calculation of Line

- 2.11.18 LIGHTING AND ILLUMINATION

The following lighting and small power arrangements shall be provided as a minimum by the Contractor.

| No | Location | Illumination Level (Lux) | Type of Fitting |
| --- | --- | --- | --- |
| a. | PV Plant Area |  |  |
|  | PV Plant Area | 20 | LED Flood light |
|  | Road or path | 10 | LED street light |
| b | 11 KV Switchyard |  |  |
|  | Around Switchgear | 50 | LED Flood light |
|  | Roadways | 20 | LED street light |
| c | Control Room cum Office Building |  |  |
|  | Control room | 500 | LED Lighting system |
|  | Electrical room and cable room | 50 | LED Lighting system |
|  | Office | 500 | LED Lighting system |
|  | Toilet, corridor, etc. | 50 | LED Lighting system |

Emergency Lighting

The Contractor shall design DC emergency lighting and power supply system for the power station, and illumination level of DC emergency lighting shall be as follows.

The lighting shall consist of 125 V DC operated incandescent luminaries.

Location 				Illumination Level (Lux)

Control room and inside 	              :		15

of control package

Inside of other package	             :		1

The other area surrounding          :		           0.5

the plant

Additional emergency lighting arrangement, independent emergency light units operated from built in charger and batteries charged by 230 V AC shall also be provided strategically. Total ten units shall be included in the Tender.

- 2.11.19 METERING SYSTEM

The metering system shall be capable of obtaining and interpreting readings and performing the adjustments, if required, to comply with the pertinent information concerning Plant performance required. The system shall be part of the Plant’s control and measurement installations, provided it complies with the criteria specified below.

Accuracy

Maximum Allowable Errors

| Measured Parameter | Maximum Error |
| --- | --- |
| Ambient Temperature | ± 10C |
| Ambient Relative Humidity | ± 3% |
| Water Temperature (when applicable) | ± 10C |
| Net Electricity (kWh) meters | ± 0.2% |
| Capacity (kW) meters | ± 0.1% |
| Time Reference | 0.01 seconds per week-maximum |

Technical Specifications of Programmable Tariff Meter

- Technical Specifications of Programmable Tariff Meter shall be compatible with BPDB automated meter reading system.

- Standard Metering Protocol for Remote Interface. 5G/4G/3G GPRS communication module with necessary accessories. Ethernet port along with RS232/485 port for communication

- Meter must support DLMS protocol.

- Optical head and software to Upload and Download of billing and analytical meter data. Software password protection facility is a must for meter programming or for Meter configuration which will be assigned and preserved by BPDB.The meter must be capable to display & record meter ID, Program, Total kWh, kVarh, kVAh, kW, kVar, kVA, PF, per phase (voltage, current, phase angle), load profile at 30 min intervals with minimum 16 channel storage data for minimum 120 days, Event log, power failure etc. Meter shall be installed at plant’s side.

### 2.11.20 CIVIL WORKS

General:

The purpose of this document is to establish the civil technical specifications.

All works included in this contract shall be executed in accordance with the bidding documents, technical specifications and other contract documents. Differing interpretations of documents shall be resolved at the discretion of the Employer BOQ

- Design and General Criteria

All civil works shall be carried out to ensure a safe operation of the plant and a design lifetime of minimum 25 years. The design shall ensure easy and low maintenance; hence maintenance effort shall be reduced with Good Engineering Practice and Design (GEPaD). Dimensions of the buildings shall provide space for a safe and proper operation and maintenance of the Plant and its equipment.

The design of all housings, foundations and structures under the described scope of work shall be such that differential and total settlements or other movements shall not exceed the limits given with the applicable codes, standards and manufacturer specification. The codes and standards generally refer to BNBC, ACI code, AISC, ASTM and LGED Building Design Standard 2015.

The dimension of PV inverter stations (prefabricated or built-onsite) and other facilities/ rooms shall be such as to provide adequate space for the safe installation and proper operation, maintenance and repair work.

The work shall be carried out by competently trained skilled labor in their various trades. International aspects and codes of safety on the construction site shall be strictly observed.

Main Road/Access Roads shall be designed to bring in all the equipment, as well as taking it out in case of maintenance or replacement. These access roads shall be suitable for the vehicles in-tended to be used during the construction phase and the maintenance period (cars, fork lifts, trucks/trailers acc. standard AASHTO HS20-44) to reach the point of equipment unloading.

Before starting with the design works, the Contractor shall submit to the Employer the project design manual containing the design data and the detailed design criteria for all civil works for approval. Detailed bearing tests and static calculations shall be conducted by the Contractor to verify the soil conditions and the related types and dimensions of the foundations. All tests and calculations shall be made available to the Employer/Employer´s Engineer for review and approval.

The following construction materials must comply with the requirements set out in the relevant codes such as BNBC, ACI Code, AISC, ASTM, AASHTO:

  - Reinforced concrete

  - Piling and sheet piling

  - Foundations and structures

  - Reinforced steel bar– round bar- deformed bar

- All Bar will be Grade 60 deformed bar

  - Concrete-Mixed designed

- Lean concrete 12 MPA

- Structural concrete 28 MPA

- Concrete Slump 50 mm to 150 mm (depending on the actual results of design mix and trial mix)

  - Geo Textile

- Geotextile fabric shall meet in full the requirement of physical, mechanical and hydraulic properties. The manufacturer must be ISO 9000 certified by an accredited register. The required porosity shall be minimum 80% and shall be protected from ultraviolet ray and any sort of damage during handling and placing. The properties shall meet or exceed the technical test values as follows:

    - Thickness 3.0 mm to 3.01 mm

    - Mass per unit area ≥ 400 g/m2

    - CBR Puncture Resistance ≥ 4000 N

    - Tensile Strength ≥ 20KN/m

  - Sand FM ≥ 1.0

- Geotechnical study

The Contractor shall be responsible for an appropriate design fitting the site conditions. Therefore, the Contractor shall perform a geotechnical survey (Standard Penetration Test (SPT) at 100 m interval to a depth of 15 m and soil samples taken at every 5 m for testing for the design of control room including drainage study and pull-out test as a basis for all design works.

The Contractor shall carry out such additional land surveys including digital topographic survey with spot levels taken every 25 m and contour lines drawn for the entire Plant site for the design of drainage network, and carry out subsurface exploration and soil investigations as required to verifying and supplement information provided by the Employer. The Contractor shall be responsible for making all due allowance for under-ground obstructions and services and for obtaining any permits, approvals and other information necessary for the satisfactory completion of the project and make such engineering works available to the Employer/Employer’s Engineer.

Pull out tests shall be strategically selected to ensure all soil conditions and worst-case conditions (such as sandy areas) are fully covered and considered in the design. A site topography survey is required prior to the start of site works. It is assumed that only some area requires fine-levelling adjustments and compaction with additional landfill.

Attention shall be paid to the water drainage measures and the erosion/flooding protection measures that may be required. When a heavy rainfall occurs, the water does not easily infiltrate the soil. If applicable, the Contractor shall conduct a drainage study before designing the drainage system.  Drainage canal and outlets (sluices) shall be designed with consideration of 25 year – 5 day consecutive rainfall.  The Contractor shall be responsible for the design of a drainage system, which avoids erosion, shall drain the water after heavy rainfall and fulfils the requirements of the site conditions according to the results of the drainage study.

The Contractor shall make his own interpretation of subsurface information provided by the Employer or obtained on his own. The evaluation of the information and its effect on the design and engineering work shall be entirely at the Contractor’s expense.

All investigations and tests carried out by the Contactor shall be in accordance with the relevant codes and standards. All tests performed at shop or at site shall be witnessed by Employer’s Engineer or his representative and results recorded.  If any defects are discovered, they shall be remedied and the tests repeated until satisfactory results are obtained.

- Topographic works

The instrument needed for this type of work is a GPS centimeter topographic accuracy and work with RTK (Real-Time Kinetic) including a Total Station and a Theodolite for digital topographic and leveling survey works.

To create a primary network database that shall work during the entire implementation period, a study must be conducted to identify survey points in the installation area.  The Contractor shall conduct fly level survey from the BWDB (with fly back for accuracy) and establish reference bench mark (in m PWD) at 3 visible permanent pillars suitably located in the project site.

The main network database shall be completed with a dense secondary network necessary to ensure coverage of all surveying needs. Before starting the work, the Contractor shall verify on the land, in the presence of the Employer, and the general plan setting out the coordinates of the vertices of the network main work base shall be signed by the representatives of both parties.

The Contractor shall be responsible for the conservation of these points, signals and markers. If in the course of the works some are destroyed, the Contractor must replace at their responsibility and expense.

First implementation must be done using main network to minimize mistakes. The main elements to consider in implementation are the foundations and the points to fix the structures, the inverters, buildings, axis of roads, axis of electrical and control canalization, electrical substation and the main equipment, and especially the perimeter of the working area.

The Contractor is obliged, whenever necessary, to stop works to perform checks with the Employer, without special compensation.

When Works finish, the Contractor shall make a final topographic check to edit the as-built drawings for submission to the Employer and shall submit a whole set of As-Built drawings of the completed works, one (1) set comprising one (1) negative drawings of the high quality reproducible polyester transparent “Mylar” film (or similar material) from which clear copies can be made and three (3) clearly printed drawings along with one set of CDs to the Employer before the expiration of the Defect Liability Period.

- Earth works

The scope of work includes Land cleaning and grubbing, Demolitions, Excavation and filling of esplanade, Trenches and pits excavations and leveling.

#### Land cleaning

This chapter includes the extraction and removal in designated areas of all trees, stumps, weeds, plants, debris, trash, land waste and any other undesirable material.

Depending on the type of terrain of each area, the amount of topsoil to be removed and poured into the dump must be determined to ensure there is no organic material.

If dumping is carried out of the area affected by the project, the Contractor shall obtain, by their means, suitable sites for this purpose, and should also provide the Employer copies of contracts with the Owners of the affected lands.

#### Demolitions

It consists of the demolition of all buildings or building elements, such as roads, buildings, concrete pieces or others needed to be removed for the execution of the work. These materials must be carried to an authorized discharge point.

#### Excavation and filling of esplanade

The materials used in the embankments come from excavations, and occasionally, when quality soil is required, external material proposed by the Contractor used in fillings for esplanades, must meet the following specifications:

- Organic material less than 0.2%

- Total soluble salts less than 0.2%

- Maximum size less than 100 mm

- Analysis according to ASTM D-422-63 - Method for particle-size analysis of soils.

- Cross sieve nº10 less than 80%,

- Cross sieve nº40 less than 75%,

- Cross sieve nº200 less than 25%.

- Liquid limit (Atterberg Limits) LL < 30 (ASTM D4318).

- Plastic limit (Atterberg Limits) PL < 10 (ASTM D4318).

The fillings shall be made of layers with a maximum thickness of 0.3 m.

After extending, the material shall be compacted to a density greater than or equal to 98% of the maximum obtained in the Modified Proctor Test (in the absence of another value in the project or Private Technical Specification), proceeding if necessary to the wetting or drying to obtain the required density.

#### Trenches and pits excavations

The excavations dimensions shall adjust to drawings, in any case, cannot be lower than these.

When performing digging foundations, axis must be centered with respect to the armatures or structure.

When the terrain features force to perform shoring, or water removal, these tasks shall be in the Contractor's scope.

#### Leveling

No slope greater than 2% shall exist on the site. The site shall be leveled in such a way that rain water cannot be logged in the project site.

#### Earth Filling

Earth filling up to the existing nearby road of the project site of Bhasanchar.

- Drainage system

The plot shall be properly drained to ensure that no water is retained inside. The rainwater drainage system shall be a network of open surface drains (with rectangular or trapezoidal cross section) and shall be designed to follow the natural flow of water and ground contours.

All the drains shall be lined with either brick or RR masonry/ concrete or stone slabs as suitable to the site conditions. The min. Thickness of the lining shall be 250 mm for brick masonry, 75mm for concrete slabs, 150mm for RR masonry and 100mm for stone slabs. The concrete slab/ stone cladding shall have suitable CM (1:4) bedding. The lining work shall be in CM (1:4) and the joints shall be raked and pointed with CM (1:3), however, the joints in peripheral drain lining shall be without pointing.

- Main roads

Main roads will connect all buildings, switchyard, BESS and transformer stations, and all other main elements of the Facility and will have a minimum width of 6m.

It is necessary to make fire-protection access roads to all buildings and structures. This kind of roads shall fulfill NFPA requirements or local requirements if mandatory.

Main roads shall be LGED Type (FRB) built using Water Bound Macadam (WBM) with surface treatment.

The compacted base coarse thickness as per design materials CBR minimum of 80%, sieve analysis as per LGED standard of base coarse resting on top of subbase coarse minimum CBR of 30 % and sieve analysis as per LGED standard of subbase coarse.

Perimeter Road

The project area will be protected by a perimeter bank. This bank shall stand at a minimum 0.5-meter high from FGL to allow their uninterrupted use during rain or flood conditions

The bank will serve as service roads, with minimum 3.0 m crest width.

It is necessary to make fire-protection access roads to all buildings and structures. This kind of roads shall fulfill NFPA requirements or local requirements if mandatory.

Main roads shall be LGED Type (FRB) built using Water Bound Macadam (WBM) with surface treatment.

The compacted base coarse thickness as per design materials CBR minimum of 80%, sieve analysis as per LGED standard of base coarse resting on top of subbase coarse minimum CBR of 30 % and sieve analysis as per LGED standard of subbase coarse.

The outer periphery of the bank (where no CC works) shall be leveled with suitable (Durva) grass, vetiver and small shrub (with no more than 7-meter height) to protect the erosion of soil of the bank.

- Internal roads

The main road network includes the roads along the perimeter, all roads connecting buildings, switchyard, inverter and transformer stations.

Internal roads (LGED Type R1) shall be Water Bound Macadam (WBM) and will connect the PV field with the main roads.

Internal roads will have a minimum width of 3m.

The internal road design must be approved by the Employer, to serve expected traffic and geotechnical subsoil characteristics, the Contractor shall be responsible to design them considering the necessities during construction and O&M.

Cross slope at roads shall be 3% to ensure that rainwater shall be discharged into drains along the path. Also, the water recollected at the longitudinal drains must be carried to a point where it could be evacuated or stored.

For designing any road, general longitudinal slope must be less than 5%. To design the radius of curves, it is necessary to consider the size of trucks to carry materials for construction (concrete, steel, gravel, sand, others), PV panels, electrical equipment (cabinet, transformers, inverters, others). At least, 15 meters of inner radius will be allowed.

The project must differentiate between the main road network and internal roads.

The rest of spaces between string and PV panels could be made leveling and compacting.

- General requirements for roads

Embankment for all roads shall have a compaction of MDD 98 % as per standard proctor, a subbase of >30 cm with a CBR >30% and a base course of >15 cm with a CBR > 80%.  A minimum safety distance between shoulder and the mounting structure shall need to be considered.

The design and execution of the roads and traffic areas shall be state of the art, functional and complete in all aspects. The roads and traffic works shall be designed, manufactured and erected according to the requirements stipulated in the latest edition of the relevant codes and standards.

All materials and testing shall be as per LGED Standards requirements, ASTM. As a minimum, the subbase material must have a CBR value of more than 30% and for Base Coarse 80% as a minimum. Rate of Compaction is considered as a minimum 98% MDD.

#### Construction

The execution of firm gravel/crushed stone layers includes the following:

- Analyze the material and obtain the working formula.

- Preparation of the surface that is to receive the gravel/ crushed stone.

- Preparation of material and transportation to the place of works.

- Extension, wetting and compacting the gravel/ crushed stone.

#### Quality demonstration

All materials shall be without clay, loam, organic material or any other that could affect layer durability. No plastic material is allowed.

The Sand Equivalent (per Standard test to sand equivalent, ASTM D2419), must be bigger than 30.

The value of the Los Angeles abrasion test coefficient (according to AASHTO T 96 or ASTM C 131), must be less than 35.

| GRAVEL SOIL | PARTICULES SIZE (ASTM D-422-63) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 ½“ | 1” | 3/4 “ | 3/8” | Nº4 | Nº10 | Nº40 | Nº60 | Nº200 |
| Cross | 100 | 75-100 | 65-90 | 40-63 | 26-45 | 15-32 | 7-21 | 4-16 | 0-9 |

A layer of gravel/crushed stone shall not be extended until it is ensured that the surface on which it is to settle has quality conditions and is planned according to tolerances.

Once the under bed is accepted the gravel/crushed stone shall be laid, in tiers of thickness not exceeding 30 cm, taking precautions to prevent segregation and contamination.

All water contribution shall take place before starting compaction. Then, the only permissible water shall be designed to achieve, on the surface, the moisture needed for the execution of the next tier.

#### Quality execution verifications

Once the road is compacted, the density must be more than 98% of the reference obtained from the Modified Proctor Test.

To ensure the capacity (load-bearing capacity) of the road, it is necessary to conduct the Elasticity modulus Test (Resilient modulus) and Plate Load Test (according to ASTM D 1196). It is necessary to measure first and second load cycle values. The relationship between both (E2/E1) must be less than 2.2 and the elastic modulus value of the second cycle must be more than 100 MPa.

The verifications of this execution must be according to LGED standards, but the analyses must have a minimum quality material of 500 m3 each, and 50 meters of road (5 density and 1 plate load test).

- Gate and Security Fence

A longitudinal fence is used to control access to the site and shall be constructed along the property boundary. The Plant shall be accessible from the main road through a gate and a pedestrian door suitably located. Security fences shall be a hot-dip galvanized chain link steel fence with commando type round barbed wire as over-climb protection. The galvanized steel fence shall consist of concrete foundations, steel poles or pillars and a wire mesh fence, the fence shall have a minimum height of 2.4m and an adequate mesh size (max. 50 mm) and additionally 0.6 m Y-shaped barbed wire over climb protection.

A gate shall be installed at the main entrance to the site. It shall consist of concrete foundation, steel poles or pillars and a wire mesh fence. The main gate shall be at least 3.0 m high and 6 m wide and shall fit the purpose with regards to width and design. Further to that, a guard house (security building) shall be provided at the main entrance.

- Switch yard civil works

Switchyard civil works shall be performed by the Contractor as per the requirements of the electrical installation of power plant and/or 11 kV substation. However, it shall be ensured that switchyard equipment’s (such as transformer, HT Panels, if required, etc.) are placed on a raised platform of minimum 9.5 m PWD. In addition, plinth and foundation for structures, equipment as per the applicable standards/ transmission utility requirements shall be taken care of. Earth pit construction shall be of brick masonry with MS chequered plate / precast RCC (1:2:4) cover. The fencing of the switchyard shall be with GI chain link of 1800 mm height with MS pipe posts. 11 kV Danger sign board should be placed outside the switchyard area. Shed at suitable height to be provided for each transformer.

- Transformer Civil Works

Transformer and equipment foundations shall be founded on piles/isolated spread footings depending on the final geotechnical investigation report.

Transformer foundations shall have its own pit which would cover the area of the transformer and cooler banks, so as to collect any spillage of oil or oil drainage in case of emergency.

The oil pit shall be filled with granite stone gravel of 40 mm size uniformly graded. The retention capacity of the transformer pit shall be min. 1/3 volume of the transformer oil which is filled with gravel with 300mm free space above gravel fill. The transformer pit shall be of RCC.

The individual transformer oil pit shall be connected to an oil collection pit which shall be sized to accommodate full oil volume of the transformer connected to it, without backflow. The oil collection pit shall be connected to oily water drainage system. Dimensions of the discharge pipe shall consider rainfall intensity also. The water shall be discharged into the nearest drain by gravity flow or pumping.

The area around the transformer and equipment shall be covered with gravel. The area shall be provided with galvanized chain link fence of height min 1.8 m and with gate. Fence post shall be 50X50X6 MS angles spaced at 2.5m c/c.

The Gate of size 3.5m shall be of MS pipe frame with welded wire fabric mesh including all accessories and fittings. MS angle posts shall conform to relevant Bangladesh Standard. The portion of the fence covering towards rail track shall be made of removable type for movement of transformer during erection / removal.

In addition a small gate, 1.2 m wide shall be provided for human entry for maintenance purpose.

Transformer track rails shall conform to relevant Bangladesh Standard. The requirement of fire barrier wall between transformers shall be as per Bangladesh Electricity Rules 1937 and relevant Bangladesh Standard.

Minimum wall thickness shall be 230mm for RCC wall and 300mm for masonry wall.

- Underground Services

#### Ditches for electrical/control cables

To install electrical and control cables, the laying of cables will be inside PVC ducts and covered by sand. To ensure the protection of tubes and cables, a minimum depth 800 mm from top of ducts is required.  It is necessary to guarantee separation between power cables (low and medium voltage) and control cables. Whenever possible, cables must be in the same level. Ducts must be marked with different colors to differentiate low/medium voltage and control.

Dimensions (width) of the ditches shall adapt to the number of ducts and cables to allow. One side in ditch is designed for power cables, while the opposite one is designed for control cables, with a minimum separation of 300 mm. In the case of medium voltage, each duct allows only one electrical circuit. The minimum diameter of tubes is one and a half times the dimensions of cable. The internal size of the tubes must be smooth.

It is necessary to install precast registers along the ditches to allow good installation and maintenance.

The sand used as a coating for medium voltage cables and copper cable is screened sand without fine grain material present in an amount that causes excessive washing by the effect of possible rainwater. The filler material shall be selected, thereby eliminating for fillings with particle sizes liable to damage the cable. The maximum size of the sand in direct contact with tubes must be 6 mm.

In the bottom of the ditch, before laying tubes, the sand bed must be ensuring a good leveling to avoid folds.

All elements in the implementation part of the trenches shall be recognized with a corresponding certificated mark quality, complying with current legislation applicable to them.

#### Drainage ditches

To ensure good rain water drainage of the working area the Contractor must design a collecting water method useful to maintain dry all the roads and ensure that water shall not accumulate around electrical equipment and buildings.

Collected rain flow must be directed to the low-level points, near the channel, at the south of the working area. Thus, all the drainage lines go from north to south.

There are several possibilities for this kind of ditches, the Contractor could choose between the most advantageous solutions considered. If the solution is an open channel, it must be of concrete, with through manufacturing or precast solution.

If the solution is to make an underground filter trench, it´s necessary dispose control registers at least every 80 meters.

In any case the two solutions must ensure, firstly, that there is no leakage along pipeline, and of course the crosses necessary to vehicles, people and any cross with other pipelines are to be considered.

- Loads

Loads are divided into categories:

- permanent load (self-weight of structure and PV panels)

- temporary loads (all other loads- imposed loads)

- Long-term load – acting for a long period (storage load, people, machinery)

- Short-term – acting for short periods of time (snow, wind).

- special loads (earthquake, explosion)

Value of overloads (temporary loads): Wind Pressure per local regulation.

Earthquake:  Per local regulation.

The buildings constructed in seismically active areas, during settlement term of operation should observe the requirements of seismic stability (horizontal acceleration and vertical acceleration due to earth quake) and provide safe stay of the people, safety of designs with earthquakes of calculated intensity.

- Steel Structures

#### Module mounting structures

The module mounting structure shall be fixed axis, ground mounted, suitable for the selected PV technology. Bidders are required to offer prefabricated mounting structures with no onsite fabrication work.

#### Codes for mounting structure design

The solar PV mounting structures and allied ancillaries shall comply with the requirements of solar PV specific standard regulations with updated amendments.

#### General

- The module mounting structure shall be fixed ground mounted, designed for applicable wind and seismic loading at the project site. Bidders shall thoroughly study the geotechnical investigation studies for the project site prior to design of mounting structures.

- Galvanized metal shall be in accordance with corrosion category C5 of EN ISO 12944-2. In any case, the Contractor shall have to substantiate that all the materials are apt for the site’s environment and conformant to local and international codes.

- Metallic bolts and fasteners shall be furnished in stainless steel with PREN (pitting resistance equivalent number) > 40. In any case, the Contractor shall have to substantiate that all the materials are apt for the site’s environment and conformant to local and international codes.

- A fixed module mounting system of designed inclination shall be used for the PV plant. The mounting structures may be indigenized with equivalent international quality standards.

- Mounting structures shall use module manufacturer recommended installation accessories like mounting clips, rails, racks etc. The design shall be approved by the module manufacturer prior to fabrication. Any such approval shall be submitted to the Employer.

- No on-site fabrication shall be permitted; all the structure members shall be factory fabricated and only assembled on site.

- The mounting structures shall be designed to maximize the energy production during the year.

#### Codes and standards

The major international codes and standards utilized during preparation of these calculations include:

##### Codes

- ACI 224R: Control of Cracking in Concrete Structures

- ACI 318: Building Code Requirements for Structural Concrete

- ACI 435R: Control of Deflection in Concrete Structures

- AASHTO: Standard Specifications for Highway Bridges

- AISC: American Institute of Steel Construction, Manual of Steel Construction

- ASTM: American Society for Testing and Materials Standards

- IEC 60721-3: Classification of environmental conditions

- EN ISO 12944-2: Protection of steel against corrosion

- Bangladeshi Code for Civil Load 2012

The Contractor may propose alternative codes and standards if a specified code or standard is not adequate for the intended purpose. In that event, the Contractor shall, as a condition precedent to its right to propose any such alternative, submit an analysis to the Employer/Employer’s Engineer for approval demonstrating that the specified code or standard is not adequate for the intended purpose.

##### Standards

The Contractor shall provide every item of the site preparation work including the following:

##### Design criteria for mounting structure

- Dead loads: Steel 77,000 N/m2

- Aluminium Extrusions 27,000 N/m2

- Solar Panel 25,000 N/m2

- Wind loads: Maximum negative and positive wind load calculate from wind speed at least 80 m/s as per BNBC-2020.

- Earthquake Zone: Considering Zone-II as per BNBC-2020 earthquake zoning Map.

All information for Design calculation regarding Wind & Earthquake to be considered from BNBC-2020.

- Steel Frames Out-of-plane deflection L/200 or 20mm, (whichever is less)

- Aluminium Frames In-plane deflection 3mm.

##### Material Specifications

The allowable stresses listed below are maximum possible values, ignoring effects of lateral and/ or buckling. Structural Aluminium, steel, stainless steel sections & plates:

Aluminium frame alloy: 6063-T5 Alloy

- Modules of elasticity 70,000 N/mm2

- Tensile stress (Fty) 110 N/mm2

- Compressive stress (Fcy) 110 N/mm2

- Shear stress (Fsy) 62 N/mm2

- Bearing stress (Fby) 179 N/mm2

Aluminium frame alloy: 6063-T6 Alloy

- Modules of elasticity 70,000 N/mm2

- Tensile stress (Fty) 172 N/mm2

- Compressive stress (Fcy) 172 N/mm2

- Shear stress (Fsy) 96 N/mm2

- Bearing stress (Fby) 276 N/mm2

Steel section and plates – Grade A36:

- Modulus of elasticity 200,000 N/mm2

- Nominal yield stress (Fy) 250 N/mm2

- Allowable bending stress (Fb) 165 N/mm2

- Allowable shear stress (Fv) 100 N/mm2

- Allowable bearing stress (Fp) 225 N/mm2

Steel section and plates – Grade SS400:

- Modulus of elasticity 200,000 N/mm2

- Nominal yield stress (Fy) 240 N/mm2

- Allowable bending stress (Fb) 158.4 N/mm2

- Allowable shear stress (Fv) 84 N/mm2

- Allowable bearing stress (Fp) 216 N/mm2

Fasteners:

- HSB Steel bolts conforming to Grade 8.8 (ASTM A325)

- Minimum ultimate tensile strength (Fu) 828 N/mm2

- Nominal yield strength (Fy) 560 N/mm2

- Allowable Tensile strength (Ft) 303 N/mm2

- Allowable shear stress (Fv) 145 N/mm2

- Stainless Steel bolts conforming to Grade A2/70

- Minimum ultimate tensile strength (Fu) 760 N/mm2

- Nominal yield strength (Fy) 448 N/mm2

- Allowable Tensile strength (Ft) 234 N/mm2

- Allowable shear stress (Fv) 135 N/mm2

#### Construction

- The mounting structures should be tested for stability with minimum deflection and sagging. Maximum permissible limit for sagging shall be 5 mm for designed wind speed.

- All connection solutions must be pinned or bolted.

- Mounting structures shall be designed to facilitate easy replacement of solar PV modules.

- Structure shall be designed with appropriate distance between two modules.

- Structure shall have provision to connect the earth cable joining one structure to the other. Connecting modules and structure to same ground cable.

- Structure design shall include a method of fastening the DC cables to the structure at every 50 cm without causing tearing or fluttering of cables.

#### Quality demonstration

The Contractor, under Employer’s Engineer supervision, and in agreement with project specifications shall demonstrate the quality of supply and workmanship on site during mounting and erection. This shall essentially include:

- Construction of civil foundations and structure: Essential quality observation shall be on the accuracy of top levels of foundations.

- Supply and installation of module mounting structure: Essential observation on structure alignments and ease of prefabricated structure erection.

- Fixing of PV modules: Essential observation shall be accuracy of module alignment, examining modules under stress and sagging effect along the length and width of mounting structure.

#### Conditions for quality demonstration

- Manufacturers / Contractor are expected to submit the quality plans and installation method statements.

- The Contractor must offer time frame for supply and installation of mounting structures in all respect.

#### Submission

In addition to the offer all the manufacturers shall submit following documents:

- Technical write-up giving complete design, specifications and information of mounting structures, material used, fabrication process, treatments performed, standards followed, types of bolts used, etc.

- General arrangement drawing of mounting structures, foundation plans, anchoring plans, overall dimensions, installation plans, structural plans and elevation and framing details.

- Standard test certificates for various structure parts from independent testing laboratories.

- In case, hot dipped galvanization thickness certificate from the factory.

- Installation method statements and quality assurance plans.

#### Warranty

A product warranty of minimum three (3) years (mounting structure, clamps, substructure, piles, etc.) shall be provided. A warranty extension – if applicable – shall be offered.

- Concrete structures and foundations

When designing concrete and reinforced concrete constructions, the required characteristics of concrete are established: strength grade of concrete, freeze-thaw durability and water impermeability grade of concrete.

#### General considerations:

Reinforced concrete according to local regulations.

The quality of the concrete used is:

- Concrete used in regularization layer: B 7.5, the property of compression strength more than 9.8 MPa. This kind of concrete cannot be used with reinforcement steel bars.

- Concrete used in reinforcement structures: B 20 F75 W4. The main properties of this type are: compression strength more than 26 MPa, and Water permeability class 4.

The value of compression strength corresponding to each class is provided in 95% of tests. The value of average strength of concrete sample (MPa) is calculated from concrete strength class (R=B/0.7635). This value is average compressive strength of a cube sample testing.

Water permeability class. It shows a maximum water pressure (kg/cm2) at which water does not penetrate through a concrete cylinder (height 150 mm). For example water permeability class W4 means that a 150 mm concrete cylinder stays water impermeable under the water pressure of 4 kg/cm2 (0.4 MPa ).

Before execution of slabs or strip foundations, it´s necessary to extend a regularization layer with pour concrete (type B7.5 according local standards), with a medium 100 mm thickness.

Sulfate-resistant Portland Cement shall be used.

Inverters and transformers shall be mounted on appropriate foundations.

Foundations PV panel structure. The Contractor must prove that the foundations and supporting structures are able to stand at least for 25 years. Foundations of PV panel Structure will be designed as per Part-VI (Structural Design) of BNBC-2020.

To guaranty durability of foundations, the minimum content of cement must be 300 kg/m3. And the maximum relationship between water/cement is less than 0.45.

The steel used in reinforcement concrete structures, must preferably be A500C (weld ability), according to local standards. With a characteristic tensile strength 500 MPa, and design value of strength 435 Mpa.

Concrete for each foundation must be poured continuously in order to avoid cold joints. The clear distance between longitudinal bars and stirrups should not exceed 300 mm in any case.

Minimum cover of 45 mm over reinforced steel in foundation in contact with ground.

The Contractor must notify the Employer before pouring any concrete, taking into account the weather, duration of transport; site status shall be discharged, etc.

The Contractor must study to the site and the concrete works to be done prior to the construction and submit the Employer a detailed plan of the concrete pouring process, including at least:

- Amount of concrete needed per day.

- Amount of raw material needed per day.

- Truck route study and number of trucks needed.

- Pouring method (pump, direct, etc)

- Designated pouring team with team leader in contact with the plant.

- Weather conditions study to predict the need for cold or warm temperatures procedures during the construction of foundations.

#### Quality. Batch plant tests:

The Contractor shall submit to the Employer documentation about the concrete batch plants they plan to source the concrete from (experience, formula, type of gravel to be used, additives, concrete used before under similar conditions).

Concrete from different plants cannot be used for the same foundation.

Plant shall analyze concrete with different dosages prior to notification to the Employer of the right formula.

Concrete specifications:

- Ratio Water/Cement lower than 0.45

- Minimum dosage 300Kg/m3.

- Slump 100 mm.

- Concrete shall be mixed in plant not in trucks.

Cold temperatures and late cure additives may be used if needed. Prior to be used, they have to be approved by the Employer.

Before construction gets started, 6 concrete samples analysis have to be done:

- 2	-	7 days

- 2	-	14 days

- 2	-	28 days

Concrete shall be accepted when:

- Concrete in good condition when it arrives to the site

- After 7 days  20 N/mm2

- After 15 days  23 N/mm2

- After 28 days  25 N/mm2

Proportioning and Designing Concrete Mixes

- Prepare mix designs for each type and strength of concrete, use proportioning on basis of previous field experience or trial mixtures. Proportion solid materials by weight, not by volume. Liquids may be proportioned by weight or volume.

When brand, type, size, or source of cement materials, aggregates, water, ice, or admixtures are proposed to be changed, new field data or data from new trial mixtures or evidence that shows that change does not adversely affect relevant properties of concrete mix.

Duration of curing process shall have to be provided to the Employer in case some additives are needed for delaying that process.

Proportion and design mixes shall result in fresh concrete with adequate workability and proper consistency to be readily worked into forms and around reinforcing without segregation or excessive bleeding under conditions of placement.

Proportion and design mixes for normal weight concrete shall result in air contents from 2 to 4 percent. Concrete where identified in Table 1 or exposed to exterior conditions subject to freezing and thawing, severe weathering, or deicers shall be air entrained having an air content of 6 percent plus or minus 1 percent.

Temporary batch plant:

- If a temporary plant is needed the Contractor shall assume the installation and operation costs.

- Curing time has to be 1 hr and 30 min after concrete is placed then time needed for transportation shall have to be calculated. List additives for cold temperatures if needed.

#### Supply control during construction:

Before placing concrete, the Contractor must check the following:

- Foundation is ready for pouring (rebar, no spills, clean…).

- The batch plant has enough material for the whole working day.

- There are enough trucks available.

- Access to the site is granted.

- Prior night- and starting-time temperatures are between limits.

Control sheet:

- The Contractor must submit daily information about the pouring process to the Employer.

- The Employer shall provide a template for the Contractor to follow this process.

Pouring the concrete:

- Records of the trucks control sheet have to be kept.

- Water cannot be added during transportation. If plasticity is inadequate, the concrete must be rejected.

- Special attention must be given to the vibrating process of concrete.

- Batch concrete analysis: 4 samples (6 cylinders each)

- 1 – 7 days

- 1 – 14 days

- 2 – 28 days

- 2 – 60 days

- External Testing Laboratory Company shall provide both, the Employer and the Contractor, with the concrete testing results at the same time.

- The Employer shall have to know in advance where and when the concrete is going to be poured. No concrete shall be poured without the knowledge of the Employer.

- Describe concrete sample cube or cylinders storage until they go to the lab, according to US Standards.

#### Execution:

##### Work preparation

- Prepare the surface below (clean, no water…)

- The Employer can check the quality of the excavation and ask that it be improved before pouring concrete.

- The Employer can check the steel reinforcement (unions, welds, distances…).

- Lean concrete characteristics B7.5

- The Contractor must construct the grounding system according to the design.

- Under bad weather the Contractor shall take special caution.

##### Formwork

- Construct formwork so concrete surfaces conform to tolerance limits.

- Use forms whenever necessary to confine concrete and shape it to required dimensions. Design, erect, support, brace, and maintain formwork to support vertical, lateral, static, and dynamic loads that might be applied, until concrete structure is capable of supporting applied loads. Also, meet local building code requirements for allowable stresses and for other loads, including live loads and wind loads.

- Clean interior surfaces of forms and interior form accessories of accumulated mortar or grout and other foreign material before each use.

- Earth cuts shall not be used as forms for surfaces unless otherwise noted or approved by the Employer.

- Construct and maintain formwork so completed concrete members and structures are within specified tolerance for size, shape, alignment, elevation, location, plumbness, and levelness. Camber formwork to compensate for anticipated deflections in formwork before concrete hardens or provides positive means of adjustment by wedges or jacks. If wood forms are used, provide means of adjustment to counteract swelling of forms where necessary.

##### Concrete mixing:

- Ready-mixed and site-produced concrete suppliers shall measure, batch, deliver, and mix concrete materials and concrete in conformance with local standards.

- Plant shall report characteristics of materials used every day. The dosage design should be reported in detail to the Employer.

- When concrete made by volumetric batching and continuous mixing is acceptable, it shall conform to requirements of Contract Documents

- Only a formula reviewed by the Employer can be used.

- In case a new formula is needed, test must be done prior to use (28 days of delay at least). The Employer shall have a week to review the formula after the testing.

- Approved mix designs shall be verified by a successful test placement onsite.

##### Transportation

- Maximum waiting time between trucks at foundation, 40 min.

- Concrete must be poured within 60 min after mixing. Additives can make longer this time but in case they are used they have to be reported to the Employer.

- Taking in account the longest trip from the plant to the farthest foundation, plant has to ensure the quality of the concrete.

##### Pouring concrete

- Name a QA/QC supervisor by the Employer.

- Do not place any concrete without approval of concrete mix from Registered Design Professional.

- If any kind of curing process, segregation or drying is founded in the concrete, it shall not be accepted.

- Do not place concrete before notifying the Employer’s Representative at least 24 hours in advance that embedded items required in particular placement have been installed, inspected, and approved.

- Concrete free fall shall not exceed 3 meters for concrete containing high-range water reducing admixture (super plasticizer) or 1.5 meters for other concrete. Thickness of the layers must allow good compaction.

- Use backhoe or directly from truck. Pumping if needed.

- Consolidate placed concrete with internal vibrating equipment supplemented with hand spading, rodding, or tamping. Use vibrators that are as large and powerful as possible without affecting proper execution. Thoroughly work concrete around reinforcement and embedded items and into corners of forms, eliminating air and stone pockets that may cause honeycombing, pitting, or planes of weakness. Do not use vibrators to move concrete within forms.

##### Pouring under cold weather conditions

- Do not place concrete during cold weather conditions without procedures approved by Registered Design Professional and Testing Agency verification of availability of equipment and materials necessary to fully implement procedures.

- Control and report of temperatures, night before, 7am, 4pm and max temp.

- If temp anytime below 3ºC

  - No pouring if temperature was below -3ºC the night before,

  - Otherwise:

  - Cover steel bars

  - Will not pour until 3ºC

  - Has to be done by 4pm

  - Antifreeze additive approved by the Employer

  - Cover foundation with isothermal blanket

##### Pouring under warm weather

- During warm weather, the Contractor shall follow the procedures.

- If over 30°C

  - Dosage report by plant

  - No pouring if over 40°0 or strong wind

  - Protect steel bars from sun before concrete is poured and then, the whole foundation

  - Avoid pouring concrete during warmer hours of the day.

##### Concrete compaction

- By vibration

- At least 2 vibrators working with 1 in reserve

##### Concrete curing

- Avoid fissures

- At least 200 gr/m2 of product qualified as ASTM C309 Type 2, or other similar.

- If fissures happen, fill with epoxy and cover with reinforced concrete

- Isotherm blankets covering the foundations if needed

- Everything must be included in the original price

##### Removing Formwork

- Unless otherwise specified, leave formwork and shoring in place to support weight of concrete in beams, slabs, and in-place structural members until concrete has reached specified compressive strength.

- Do not remove any formwork supporting the weight of concrete or construction loads until the concrete has attained 75% of its specified design strength. If lower compressive strength is proposed for removal of formwork, submit detailed plans for review and acceptance. Analysis methods and results shall be submitted for approval before early formwork removal. Such analysis shall be at the Contractor's expense

- When removal of formwork is based on concrete reaching specified compressive strengths, formwork may be removed when either of the following requirements is met:

  - Test specimens, field cured under the same moisture and temperature conditions as the concrete they represent, reach the compressive strength specified for formwork removal. Mold samples in accordance with local standards and cure them under same conditions for moisture and temperature as used for concrete they represent.

  - Concrete has been cured as specified for the same length of time as laboratory-cured specimens that have reached the compressive strength specified for formwork removal. Determine the length of time concrete has been cured in the structure by the cumulative number of days or fractions thereof, not necessarily consecutive, during which the ambient air temperature is above 10°C and the concrete has been damp or thoroughly sealed from evaporation or loss of moisture.

- When finishing is required, remove forms as soon as removal operations shall not damage concrete.

- Do not remove forms early unless all the following are met:

  - Shores and other vertical supports to remain are arranged to allow removal of side forms without loosening or disturbing shores and supports.

  - Concrete has cured at least 24 hours, not necessarily consecutively, above 10°C and concrete has hardened sufficiently to resist damage from removal operations.

  - Unless they support only the lateral pressure of plastic concrete or strength criteria is met.

- Cure and protect formed surfaces exposed by the early removal of formwork in the same manner as unformed surfaces for the remainder of the specified curing and protection periods.

- Patch tie holes and defects of all formed surfaces before finishing, except that fins, burrs, and other projections may be removed, as specified for finish type, concurrently with patching operations.

- Clean and repair surfaces of forms to be reused, including removal of old form release agents and accumulated concrete mortar. Dispose of split, frayed, delaminated, or otherwise damaged form facing material.

##### Joints

- Every 5 m in slabs or pavements

- No contact between different cement concretes if inconsistent

- No concretes from different plants in the same foundation

##### Finishes

- Good appearance

#### Liabilities

- No inspection, visit, writing or verbal approval for formulas, additives, authorization to proceed, shall reduce the liability of the Contractor to ensure the concrete quality.

- All expenses to achieve the quality demanded here (blow the foundation, reworks, etc.) must be paid by the Contractor.

#### Materials

Cement Materials: Use cement materials that are of same brand and type and from same plant of manufacture as cement materials used in concrete represented by submitted field test records or used in trial mixtures. Unless otherwise specified or permitted, use moderate heat of hydration Portland cement, blended hydraulic cement with moderate or low heat of hydration properties, or Portland cement combined with fly ash or blast furnace slag (Cement materials shall conform to ASTM C150 Type V for standard (28-day) strength concrete, high sulfate resistance or the local equivalent standard).

Aggregates: Aggregates shall conform to local regulations, unless otherwise specified.

- Aggregates used in concrete shall be obtained from same sources and have same size ranges as aggregates used in concrete represented by submitted historical data or used in trial mixtures.

- Do not use aggregates that are classified as "moderate stain" or darker, when tested for staining

- Furnish largest size coarse aggregate consistent with cover and clearance requirements. Furnish in two separate component sizes until mixing in concrete.

- Materials

  - Coarse aggregates for normal weight concrete shall be crushed stone, crushed gravel, or washed gravel conforming to local standards.

  - Fine aggregate shall be natural sand.

Water and Ice: Mixing water for concrete and water used to make ice shall meet requirements.

- As a general requirement any water, successfully used before, could be applied.

- If there is no evidence of had being used before, it would be rejected if do not agree:

- pH ≥ 5

- DS ≤ 15000ppm

- Sulfates as S042- ≤ 1000ppm (but if cement used is sulfates resistant)

- Concentration of Cl-

  - If prestressed concrete ≤ 1000ppm

  - If regular concrete ≤ 3000ppm

- Carbohydrates = 0

- Organic matters soluble in water ≤ 15000ppm

- Constructions

#### Buildings

The Contractor shall design all buildings according to Bangladeshi Standard Regulations. The buildings need to be equipped with cooling systems where required. The cooling systems need to be designed in a way that it fulfils the allowed operation temperatures of the equipment installed in the buildings. All required ambient conditions of the different equipment need to be met.

The Contractor shall provide all required buildings. All building structure designs are conducted in accordance with local building standard and local statutory requirements.

The Contractor shall be responsible for all necessary local government approvals and permits for construction of the buildings and structures.

All buildings shall be built at sufficient height over ground level to ensure that they shall always stay above the maximum recorded water level on the site.

##### Types of Buildings

The Facility shall comprise of the following buildings:

- Control room cum Administrative Building:  There will be a 4-storied building with at least 225 sqm floor size each. The first floor shall be used for the installation of switchgear and O&M purposes, and the second & third floors will be used for accommodation & administrative purposes. The height of the ground floor will be 12 feet, 1st floor will be 14 feet, 2nd & 3rd floors will be minimum 10 feet.

### Ground Floor

- Spare Parts Room: Secure room for consumables, tools, and accessories, with racks and cabinets.

- Safety and Compliance: Smoke detection, fire suppression, drainage, earthing, and cable trays with shock-proof mats.

### First Floor

- Control Rooms: Two separate rooms: one for 11 kV Generation Switchgear and one for 11 kV Distribution Switchgear, with adequate space, ventilation, and air conditioning for reliable operation.

- Office Rooms: Two fully furnished offices for operational and administrative staff, equipped with 2 desks, 6 chairs, 2 four-drawer filing cabinets and LAN/WAN connectivity. Each office room will be equipped with one PC (CPU: e.g. minimum Intel Core i5, 3 GHz 64Bit & 8 GB RAM) with 19.5 inch monitor.

- Restroom: Modern facilities for staff.

- HVAC and Safety Systems: Air conditioning (at Control room area), proper lighting, ventilation, smoke detectors, and fire protection measures.

### Second Floor – Administrative Purpose

- Office Rooms: Four office rooms with attached bathrooms, 1 furnished with executive desk, 1 swivel chair, 3 visitor seating, 1 filing cabinets for each room. One executive office includes bookshelf or side table for managerial functions. Each office room will be equipped with one PC (CPU: e.g. minimum Intel Core i5, 3 GHz 64Bit & 8 GB RAM) with 19.5 inch monitor and a printer

- Conference Room: One conference room for 20 persons, with conference table, chairs, and presentation facilities (Projector & Screen).

- HVAC and Safety Systems: Air conditioning (at 2 rooms & Conference room), proper lighting, ventilation, LAN/WAN connectivity, and safety systems including smoke detectors and fire protection.

### Third Floor – Emergency Support Service (Accommodation)

- Accommodation Rooms: Five fully furnished rooms for on-site staff of 24 hours emergency support.

- Furnishings: Each room includes semi-double bed, bedside table, wardrobe or closet, study desk with chair, adequate lighting, air conditioning, and ventilation.

- Facilities: Attached bathrooms with modern sanitary fixtures and a common kitchenette for basic food preparation and storage with dine in facilities.

- HVAC and Safety Systems: Air conditioning (at 2 rooms), proper lighting, ventilation, LAN/WAN connectivity, and safety systems including smoke detectors and fire protection.

### Furniture and Fixtures

“All furniture shall be of premium quality, constructed from durable materials with excellent workmanship, conforming to relevant international standards. Materials, finishes, and fittings shall be approved by the Engineer prior to installation, ensuring long-term functionality, aesthetics, and user comfort.”

Water System of Control Cum Office Building:

The Control Room cum Office Building shall be equipped with a reliable water system including an overhead water storage tank and pressurized distribution piping (using CPVC or PPR pipes) supplying potable water to all fixtures—such as toilets, washbasins, showers, kitchen sinks, and security room outlets. Sanitary fittings will include dual-flush toilets, sensor-operated faucets, and floor drains in wet areas connected to a closed drainage system with PVC pipes leading to the main sewage or septic tank. Hot water will be provided via electric or solar water heaters with thermostatic mixing valves for temperature control. Drinking water points will have inline filtration units (e.g., UV or activated carbon filters) to ensure water quality. The system will also include gate valves and automatic pressure pumps for flow regulation, as well as emergency shut-off valves for safety and maintenance.

The Tenderer has to submit the proposed drawing of control room building along with the bid to the owner for approval. The building shall be designed to meet national building code requirement. The control Room shall be provided with suitable smoke detectors and the entrance of the control room shall have ramp arrangement for the entry of goods and the necessary cable to be brought through cable tray arrangements. All the cable trays shall be provided with shock proof rubber mats.

- Inverter Station: It includes the house of string inverters.

- AC Distribution Board: It comprises low voltage Air Circuit Breaker (ACB) and associated breaker & accessories.

- Diesel Generator station/Room: Sufficient space for station with proper ventilation, fuel piping form Diesel storage Tank and required power evacuation system.

- Transformer Station: It includes pulling transformers and associated accessories.

- Battery Energy Storage System (BESS): BESS shall include battery and associated equipment.

- Security Guard Room:  There will a security guard room at the main gate on the access road and the main entrance to the office areas. There will be few watch towers at the remote boundary of the power plant site.

All buildings forming part of the Project must be designed and constructed for the purposes of the Project and in accordance with Bangladeshi standards and specifications and, as a minimum, the following requirements:

- All foundations must be compacted up to minimum 95% of MDD and with lean concrete, ground slab subgrade/ formation level to be compacted up to 95 % of MDD.

- Must have finished interior and exterior, electric wiring, plumbing, sanitary facilities (as required), wiring for LAN and telephone and air conditioning or ventilation as required;

- Must have sufficient space to install any components required under the Bangladeshi regulations or laws

- Air-conditioning for all houses and rooms with personal and/or electrical appliances is mandatory.

- Must include energy saving features, such as shades, ventilation, high efficiency lighting fixtures, proper selection of material for the windows and doors, motion sensors for lighting control;

- Must blend into the local environment rather than stand out;

- Must be adequately weather proof taking into consideration the local conditions (i.e. sand storms, cyclonic storm, heavy rain, humidity, temperature, etc.);

- Must have an operational and suitable fire alarm and protection system as follows:

- All buildings must be fitted with smoke and heat detectors to protect personnel, environment and equipment which comply with the local Fire Code;

- The system must include acoustic (bell) and optical (strobe light) devices to signal a fire hazard;

- The system must include the following devices:

- In the main building: a main fire alarm panel and graphic annunciators to indicate the location of the alarm in the building;

- In all buildings: addressable smoke detectors, addressable heat detectors, network reporting terminal, conduit/trucking and fire-resistant cabling;

- Must ensure the roofs have waterproofing system, including a minimum slope of 3% to provide adequate runoff for rainwater and are fitted with gutters and steel down pipes with a finish color coating matching that of the wall panel base color; and must have railings for safety, where-in the materials to be used shall be coated for protection against rusting as minimum powder coated or equivalent.

- Must have permanent access ladders or stairways and platforms, wherever necessary, to permit the successful operation and maintenance of the facility.

- Must be elevated above ground level according to local standards to ensure protection from sand on the site according to actual site conditions as determined during site preparation and construction and subject to review and approval by the Employer;

- Must be tailored to the operational and technical requirements of the equipment installed there in;

- Wherever possible the building height and location must be optimized to prevent any shading of the modules.

Buildings forming part of the Project must include:

- Access ways or openings for maintenance of sufficient height and width to enable the installation and removal of the largest item of equipment within the relevant building;

- Personnel doors at all necessary locations within the relevant building; and

- Regarding the air-conditioned buildings, hydraulic door closers on all doors in airconditioned areas of such building, and all doors/openings shall be blast resistant, must be robust and able to withstand damage from wind and other forces that may be encountered at the site.

Cable, pipe and service openings through floors and walls must be designed that, after installation of the cables or pipes, these service openings must be sealed, smoke-proof and fire-proof. The sealing materials used for this purpose must be fire resistant and easily removable in the event of installation of further cables or services in the future.

Noise, vibration and temperature levels in all buildings must be within permitted limits.

The dimensions of the buildings shall be such as to provide space for a safe and proper operation and maintenance of the Power Plant and its equipment.

Permanent access ladders or stairways and platforms shall be provided for maintenance and operation of equipment, wherever necessary.

Access ways and openings for maintenance shall be sized according to installation and removal of the largest items inside the Power Plant. Personnel doors shall be provided at all necessary locations.

Access to the storage area shall be direct from outside and inside.

##### Control Building

The control building shall include separate rooms for:

- Main Electrical equipment

- Operation and Maintenance Works

- Storage of spare parts

- Security room.

- Toilet / washroom area (one each for male and female)

The design of the switchgear room must be in accordance with applicable national and international standards. This includes a minimum distance of the equipment to each of the interior walls of the room, as well as fire proof walls.

Based on the selected switchgear and the pressure relief execution, pressure relief provisions have to be provided, in accordance with the switchgear manufacturer, national and international standards.

The switchgear relief pressure shall be limited to 1,600 Pa. However, it has to be proven that the building, walls, ceiling, floor and others are designed for the maximum occurring pressure.

The auxiliary transformer can be erected on a separate transformer platform or pole mounted (auxiliary transformer) outside the control building.

If the transformer is integrated into the control building, sufficient fire protection, pressure reliefs have to be implemented.

Flooring for the Switchgear and the transformer shall be double floor type with ≥ 10 kN, minimum class 5, according to DIN EN 12825.

The switchgear room and the control building must comply with standard DIN EN 61936.

The water proof underground septic tanks for sanitary wastewater shall be provided.  The tanks will be provided with aeration system to treat, and dispose of wastewater within the septic tank.  The Contractor shall ensure that the discharged treated domestic wastewater is compliant with the current standard adopted by Department of Environment following national rules and/or regulations.

The Contractor shall construct a car park in front of the building for a minimum of 10 cars.

Concept drawings for all buildings shall be provided with the bidding documents confirming room sizes, main architectural and structure materials.

#### Separation of Installation

The arrangements of electrical components installation of Low Voltage and Medium Voltage have to be physically separated with sufficient space for maintenance purpose.

#### Solar power field construction

The solar field consists of solar blocks, containerized inverters and transformers. Containerized inverters and transformers shall be mounted on solid reinforced strip foundations made of concrete based on sulfate-resistant Portland cement. 100 mm concrete bed (B7.5 concrete) shall be laid under strip foundations.

The containers for inverters and transformers can be either prefabricated enclosures or pre-cast concrete buildings.

# Test Requirements and Acceptance Criteria

This chapter specifies the minimum technical requirements for testing of materials, parts, equipment and workmanship of the plant during assembly, erection and upon completion to demonstrate compliance with the specification, codes and standards and to ensure overall availability and reliability of plant operation and performance. All test shall, as a minimum, comply to the below listed items, comply with the Solar Grid Code and furthermore ensures to be in correspondence with latest industry standards.

All works supplied under this document shall be adequately inspected and tested through visual, material, non-destructive, and functional and performance inspection, tests during manufacture, after delivery on site, during erection and after erection completion on site. The Employer reserves the right to witness the main equipment manufacturing tests and the Contractor shall facilitate and coordinate the same.

The Contractor shall prove through the issuing of test records and reports, that all material and equipment comply with the requirements of the specification and is in accordance with the applicable codes and standards and has successfully passed all inspections and tests.

To ensure a proper operation of the Plant, all necessary tests shall be per-formed on the PV modules, inverters, cables and additional equipment such as electrical systems and PCMS equipment, etc.

Precondition for starting the tests on completion of the Plant are the availability of complete design documentation including as built drawings, string measurement protocols, availability of plant operation and maintenance manuals and a fully operating monitoring system including on site meteorological measurement station.

All measurements and testing results shall be presented within the individual commissioning reports including details of the tests and shall at least include the list of the measurement equipment, responsible engineers and timestamps.

For each of the specified acceptance and performance tests, the Contractor shall evaluate the test figures and data within two (2) weeks of the completion of the relevant test. Two (2) copies of the test report containing a complete analysis of the result and performance evaluation shall be submitted to the Employer/Employer’s Engineer for approval. Softcopies of the test reports shall be also provided.

The Contractor is responsible for performing the necessary testing and passing the tests required by the grid operator as per the requirements and procedures mentioned in the Bangladesh Electricity Grid Code, 2018. As per documents, these tests are mandatory for achieving the Commercial Operation Date.

## CODES AND STANDARDS

Where no specific code or standard is mentioned in the specification, the various components of the Plant shall be tested in accordance with the relevant international or/and national standards. IEC standards are compulsory for the electrical equipment. Tests shall also be carried out in accordance with the Bangladesh Electricity Grid Code, 2018 and with the manufacturer's standard codes of practice and recommendations shall be approved by the Employer/Employer’s Engineer.

## WORK PROGRESS INSPECTION

The Contractor is responsible for the provision of at least the following information to the Employer/Employer’s Engineer on frequent basis:

- Internal quality inspection reports of materials delivered by the suppliers for all main components

- Production progress report

- Building progress reports

## TEST EQUIPMENT

All equipment for (performance) tests shall be supplied by the Contractor and shall be retained by him upon the satisfactory conclusion of all such tests at site unless otherwise specified in this document. All costs associated with the supply, calibration and installation of the instrumentation devices for performance testing of the plant shall be included in the contract price.

All test instruments shall be supplied with up-to-date calibration certificates issued by an accredited independent testing laboratory. The difference between the certification date and the actual performance test start date shall not be greater than 90 days.

## FACILITIES FOR TESTING AND RELATED

If the approved test procedures require any third-party participation, special facilities to conduct the testing, test or / and endorsement of inspection and test results, the Employer reserves the right to select the necessary party while the Contractor shall be responsible for arranging and coordination of all necessary tasks.

The Employer reserves the right for inspection visits and expediting in addition to the Contractor's testing program to monitor the progress and quality of the works. In the event that such additional inspections and tests indicate non-compliance with the terms of the contract, the Contractor then shall at his own expense, make all necessary repairs and perform additional test(s) required to meet the compliance with the terms of the contract.

## REJECTION DUE TO TEST RESULTS

If any item and / or component fails to comply with the requirements under this document at any stage of the design, manufacture, factory testing, works test, site erection, site testing, commissioning and performance testing, the Employer reserves the right to reject the item, or defective component. The corrective action shall be performed by the Contractor as instructed by the Employer/Employer’s Engineer and the Contractor shall submit an official letter for further inspection and/or test. In the event of a defect on any item, the item shall be replaced by the Contractor at his own expense.

No extension of time or extra costs shall be considered as a result of repeated tests or material/equipment rejection.

## FORMAL REQUIREMENT FOR INSPECTION AND TESTING

### 3.6.1 Inspection and Testing Program

Within ten (10) days after receipt of the Notification of Award (NOA), the Contractor shall issue a quality assurance program, indicating the kind and extent of all inspections and tests to be carried out on plant components subject to be approved by the Employer/Employer’s Engineer. The quality assurance program shall be based on the tests and inspections specified in the various parts of the specification.

An Inspection and Test Plan (ITP) shall be prepared by the Contractor and shall be approved by the Employer/Employer’s Engineer. The ITP shall detail the scope and schedule of the inspection required ensuring that dispatched materials meet the specification requirements.

A. Pre-delivery Inspection and/or witnessing of the manufacturing process and tests of the equipment at manufacturer's works including transfer of technical know-how:

The Employer and the Project Director or their designated representatives shall be entitled to attend the aforesaid test and/or inspection as stated in the Technical Specifications, and the Contractor shall bear all costs and expenses incurred in connection with such attendance including, but not limited to, all traveling and board and lodging expenses. Furthermore, all equipment which to be manufactured locally shall be subject to pre-shipment inspection.

The Contractor shall give a reasonable notice to the Project Manager 90 days or 3 months earlier whenever any such parts of the Facilities are ready or about to be ready for test and/or inspection; such test and/or inspection and notice thereof shall be subject to the requirements of the Contract.

The Contractor would not be relieved from its responsibility/ liability of making appropriate plant and material as per Specification despite inspection by the Employer/ Project Director or their designated employees.

The Contractor shall at its own expense carry out all such tests and/or inspections at manufacturer’s premises for (1) PV Module, (2) Inverter, (3) Transformer, (4) PCMS System, and (5) BESS

The Engineer and Board’s authorized representative shall have the right to inspect and/or to test the Goods at Site and at manufacturer’s premises to confirm their conformity to the Contract. The cost of performing any tests shall be borne by the Contractor. The payment for inspection and tests at the manufacturer’s premises and training on tests including traveling expenses, daily pocket expenses (@ US$100-/person/ day) and lodging at actual for seven days/ Inspection (Except the travelling time). The cost of subsequent inspection(s) due to rejection/additional re-testing of Goods at the first inspection shall also be borne by the Contractor.

Total 09 (nine) nos. of Engineer (nominated by the Purchaser) in three groups (Engineering Team) will participate on the quality acceptance test (QAT) for the offered equipment at the manufacturer's plant and confirm their quality as per specification.

| Group | Nos. of Engineer | Name of the Equipment |
| --- | --- | --- |
| Team-1 | 03 | PV Module |
| Team-2 | 03 | Inverter & Transformer |
| Team-3 | 03 | BESS, PCMS System |

Third Party Inspection:

For any reason, if Purchaser’s/ Employer’s representative(s) cannot attend Inspection/ Test program described in PCC [GCC 23.1], a Third-Party Inspection Company/Agency shall conduct/ witness above mentioned Inspections/Tests as per Contract and relevant standard at the Manufacturer’s Premises with the concurrence of BPDB. The Third-Party Inspector shall submit a comprehensive report to Purchaser with recommendation accompanied with photograph and video clips with date and time of the Equipment/ Materials/ Goods inspected within 7 days after completion of respective inspection/Test. After approval of Third-Party Inspection report by BPDB, shipping advice shall be issued to Supplier/ Contractor. No Equipment/ Materials/ Goods shall be shipped without shipping advice.

The inspections/ Tests shall be performed on as-needed basis as per schedule provided by the respective manufacturers.

Supplier/Contractor/ Manufacturer shall not claim any additional cost for Third Party Inspection. The third-party inspection company/agency must not be involved in design, procurement, fabrication, construction and installation under this Contract.

BPDB Shall choose/ propose any of the following companies/agencies as Third-Party Inspector:

1.	BUREAU VERITAS,

2.	SGS,

3.	Black and Veatch,

4.	TUV SUD,

5.	Lloyd Inspection Agency,

6.	Mott MacDonald,

7.	Intertek group,

With the approval of BPDB, Contractor/Supplier shall engage Third Party Inspection company/ agency. BPDB reserves the right to revise above mentioned list.

Third party inspection is applicable for Equipment/ Materials/ Goods manufactured in outside Bangladesh.

B. Receiving cum Damage Report:

(a) Receiving cum Damage Report shall be done after arrival of the materials/ equipment/Spare parts at Bhasanchar, Noakhali, Bangladesh. The program of such Inspection shall be intimated to the representative of the Contractor by BPDB upon arrival of the materials/ equipment at project site.

(b) The Purchaser has right to inspect, test and where necessary, reject the Goods arrival in the purchaser’s store shall in no way be limited or waived by reason of the Goods having previously been tested and passed by the manufacturer/supplier. The contractor will facilitate such Inspections/ Tests. If any equipment do not conform to the terms and specifications of the Contract Agreement, those shall be rejected. In such cases, the Contractor shall bear all costs related to the return and replacement of the non-conforming equipment, including but not limited to transportation, re-importation, Customs Duty, VAT, and any other applicable taxes or charges.

(c) Nothing in this clause shall in any way release the supplier from any warranty or other obligation under the provisions of the contract/purchase order.

### 3.6.2 Construction Progress Inspections and Certifications

The Employer and/or its authorized representatives are irrevocably entitled to inspect any equipment upon arrival at site, under erection or commissioning at site at any time without prior announcement to inspect the works performed in connection with this project and to monitor the progress of work, scrutinize related documents and to take photos as may be deemed adequate to the judgement of the said persons to document the actual status of work.

All tests shall be accompanied by the test records signed by all parties. In case of tests involving also activity of other contractors all remarks and comments shall be placed in the test record signed by all participants.

Erection and construction checks/tests shall be announced and carried out after completion of the electromechanical installation works.

A punch list shall be generated during random progress visits by the Employer/Employer’s Engineer. Prior to each official site inspection witness by the Employer this punch list shall be submitted along with Request for Inspection (RFI) to the Contractor. Such punch list shall include a brief description of identified deficiencies, the corrective work to be per-formed and items classification in three (3) categories:

- Category A major default shall be fixed with undue delay and before acceptance and transfer of risk.

- Category B minor defects but negative impact on yield production and therefore shall be fixed before acceptance and transfer of risk.

- Category C minor defects without negative impact on the yield production within 1 months after acceptance test and before Taking Over.

When a system or part of the Facilities is completed, the Contractor shall notify in writing to the Employer that an inspection should take place to determine that the concerned system is installed according to the specifications and according to the approved drawings.

### 3.6.3 Staffing

During commissioning, the Contractor shall nominate and make available the person responsible to supervise and manage their staff.

The Contractor shall provide a team of suitably qualified and experienced technicians to pre-commission and commission the overall plant.

The Contractor shall ensure at all times that his staff and any subcontractor or seconded staff shall observe all prescribed safety rules and regulations.

### 3.6.4 Test Procedures and Testing Program

The development and implementation of test procedures for the construction, inspection, commissioning, start-up and performance testing of the Plant shall be the responsibility of the Contractor and shall be performed in accordance with the plant description, design conditions and technical data. The inspections, tests, commissioning, start-up and performance procedures and method statements shall be approved by the Employer/Employer’s Engineer. All tests except where third-party involvement is required, shall be performed by the Contractor or his authorized representative and witnessed by the Employer/Employer’s Engineer.

The overall testing program for the Plant shall consist but is not limited to the following:

- Inspection, testing, start-up, operating tests and acceptance of the electrical systems and sub-systems.

- Inspection, testing, start-up and operation testing of the Plant, related equipment and systems.

- Inspection, testing, start-up and operation testing of the BESS, related equipment and systems.

- Inspection, testing, start-up and operation testing of the Distribution System, related equipment and systems.

- Inspection, testing, start-up and operating tests of plant auxiliary equipment such as Plant Control and Monitoring System (PCMS), security system, Energy Meters, etc.

- Acceptance tests.

All testing activities for the electrical facilities of the Plant shall be implemented and coordinated with the testing and commissioning of the installed equipment and components.

The Contractor shall submit a description of all relevant test procedures in written form. The description shall be submitted to the Employer and shall include but not limited to:

- Test programs and schedules

- Test standards

- Type of inspection and tests

- Check lists

- Description of instrumentation to be used during testing and calibration of test results

- List of the tests which shall be witnessed by third parties

- Quality control procedures

- Forms of test records and reports

Formulas, correction factors and methods used for adjustment to reference site conditions, which it shall be approved by the Employer/Employer’s Engineer.

### 3.6.5 Commissioning

The Contractor shall be responsible for the safe and efficient setting to work on the entire Plant and equipment. The methods adopted on site shall be in accordance with all applicable safety and permit regulations. The Contractor shall submit, a comprehensive commissioning manual detailing the approach for individual system/subsystem commissioning, all preparations for the start-up of the entire Plant and execution of reliability and performance tests for the Employer/Employer’s Engineer approval.

The condition for allowing any system or equipment to be operated requires the successful tests on completion, documented by a duly completed and countersigned erection checklist.

The Contractor shall give sufficient detail in the commissioning program including the sequence and duration of the works in a logical and realistic way.

At latest before the start of the construction phase, the Contractor shall submit for approval comprehensive schedules of the commissioning checks. The schedules shall then be used during commissioning as a guide for the methods to be followed and to record the actual activities carried out with commissioning date. The Contractor shall also submit for approval all schedules of commissioning procedures. These schedules shall detail the necessary tests to ensure the complete and satisfactory commissioning of each section of plant and shall detail operational limitations. The schedules shall be used during commissioning, which shall only commence when the previous checks have been completed successfully.

The schedules shall be updated regularly by the Contractor and a revised copy submitted to the Employer for approval.

Each activity on the commissioning procedure schedules, when completed to the satisfaction of the Employer shall be signed and dated by the Contractor and shall be countersigned by the Employer.

The commissioning procedures and schedules shall ensure that the commissioning of any item of the work does not interrupt the normal operation of any previously commissioned item or any item to be commissioned jointly with equipment of other areas.

When the commissioning of each sector is completed and before the trial operation period or tests on completion are commenced, the Contractor shall carry out such preliminary electrical tests as necessary to establish that the Plant is functioning correctly and efficiently and shall make any adjustments and/or optimizations as required.

The Contractor shall ensure the commissioning completion by performing a joint walk down together with the Employer, Employer’s Engineer, representatives of the network operator, if required, to generate a punch list report on a system, listing and identifying the outstanding items and/or corrective works to be performed as well as their priorities.

All test equipment, tools, materials, consumables, labor and spare parts required during commissioning shall be provided by the Contractor.

### 3.6.6 Commissioning Tests

The commissioning tests start after completion of the plant’s facilities and the once the interconnection to the substation is fully operational.  The Contractor shall perform the tests in accordance with approved procedures. The Contractor shall provide all the personnel, test facilities, equipment and tools to assist with the Commissioning works. The test procedures and schedules shall be submitted by the Contractor to the Employer/Employer’s Engineer for approval at least three (3) weeks prior to conduct the tests.

The testing shall prove that the Plant (mechanically and electrically) and the PCMS meet all the specified requirements and be well functional. The plant performance test shall be commenced upon the commissioning works have been successfully completed.

- String Commissioning

String commissioning involves visual inspections as well as tests and measurements to verify the safe and proper operation of the system. The verification shall be carried out in according to the IEC 62446.

The Contractor shall procure qualified and experience personnel to execute the tests. The Contractor shall provide sufficient safety training and appropriate personnel protection equipment to all staff involved.

The Contractor shall check PV modules and cables to ensure that damage or deteriorate is not detected. The Contractor shall check that all the cables are tied properly and neatly. If there is any defect was found in any string or any component, the Contractor shall rectify the defect as soon as possible, the string test shall not be carried out till the rectifying works has been accomplished. The Contractor shall also check that all strings have been labeled appropriately and collect.

The Contractor can carry out the test after the inspection has been completed.

The Test shall be conducted with the appropriate apparatus and in accordance to the proper procedure. The following test shall be performed:

- Continuity of equipment grounding conductors and system grounding conductors (if applicable) – where grounding conductors are fitted on the DC side, attach with the mounting structure, an electrical continuity test shall be made on all such conductors. The connection to the main earthing terminal should also be verified.

- Polarity of all dc cables and check for correct cable identification and connection – the polarity of all DC cables shall be verified using suitable test apparatus such as multimeter.

- Open-circuit voltage [Voc] for each string – the open circuit voltage of each string shall be measured using suitable measuring apparatus. For multiple identical strings scenario, the voltages between strings shall be compared and the values should be similar, under stable irradiance conditions. The string shall be verified that operating parameter is within specification.

- Short-circuit current [Isc] for each string – the short circuit current of each string shall be measured using suitable measuring apparatus. For multiple identical strings scenario, the currents between strings shall be compared and the values should be similar, under stable irradiance conditions. The string shall be verified that operating parameter is within specification.

- Insulation resistance – the test demonstrates a potential electric shock hazard. This test verifies the integrity of wiring and equipment, and used to detect degradation and faults to wiring insulation. Test methods are (i) test between array negative and earth followed by array positive and earth, and (ii) test between The Contractor shall provide test report, which the documentation of the report should include the following items:

- Single Line Diagram of tested strings; and

- Inspection and Test Results

The Contractor may use the commissioning string procedure and methodology for periodic string verification during operation.

- THERMOGRAPHY TEST

- Thermography Test for Solar PV Modules

The Infrared Thermography test shall identify unusual temperature differences during operation of the solar modules to diagnose thermal and electrical failures in PV modules, such as identify defective cells, bypass diodes, solder contacts, etc. A minimum of 5% of the entire plant shall be measure as a sample.

The measurement shall be done in accordance to IEC 62446. The insolation onto the module array area shall be not lower than 600 W/m² with low wind speed. The angle of view should be set as close as possible to 90° but not less than 60° to the module glass plane. Only an experienced operator, i.e. certified as ITC Cat 1 Thermographic operator (ISO 18436-7), shall conduct the test. Cell temperatures within a module shall not differ more than 5 Kelvin. In case discrepancies appear, the check shall be expanded to the backside of the module.

In case defective modules are identified, such modules shall be exchanged on the Contractor´s expenses and the test shall be extended to 100% coverage.

- Thermography Test for BOS Components

BOS components, including Combiner Box, Inverter, Transformer, AC Switch Cabinet Cables and Cable Connectors shall be detailed checked with a Thermography Camera on 100% basis. Abnormalities shall be evaluated with the Employer/Employer´s Engineer and fixed in accordance to the recommendations of the Employer/Employer´s Engineer.

- Acceptance Certificate:

Operational Acceptance Certificate:

The Operational Acceptance Certificate (OAC) shall be issued upon successful completion of the project  “Technical guarantees” as specified Bid Volume III.

The Contractor shall carry out the Guarantee Tests and ensure compliance with the Technical Guarantees in accordance with the provisions specified in Technical Guarantee Parameters of the Contract Agreement. The Contractor shall comply with all Technical Guarantee parameters in order to be eligible for issuance of the OAC (Operational Acceptance Certificate).

Final Acceptance Certificate:

For the issuance of the FAC, the Contractor shall successfully achieve the desired outputs of the FAC-related tests as specified under the Technical Guarantee Parameters. From OAC to FAC, the Contractor shall maintain a minimum of two site engineers on-site for supervision.

# QUALITY aSSURANCE pLAN

The Contractor shall follow a Quality Assurance Plan complying the following.

## CONTRACTOR DUTIES

  - The Contractor shall establish and staff a Quality organization meeting the requirements stated in the following chapter, with qualified resources to effectively administer and implement the requirements.

  - Ensure Quality is built into the Work product through use of documented control processes that incorporate necessary activities to assure Quality.

  - Verify Quality throughout the Work, including verifying Work performed by Subcontractors, Vendors, and Sub vendors.

  - Provide Quality Assurance for the Work, consisting of all those planned and systematic activities that are necessary to comply with Quality requirements and to provide confidence that the Work shall conform to established requirements and perform satisfactorily in service.

  - Provide Quality Control for the Work, consisting of those Quality processes, procedures, operational techniques, and activities that provide the means of measuring and controlling the characteristics of an item, element, component, product, service, or installation to meet the established requirements.

  - Identify, report, control, and resolve deficiencies (nonconforming processes and items) detected during the execution of the Work including Subcontractor(s), Vendor(s), and Sub vendor(s) Work activities.

  - Produce documentation to demonstrate the Quality of Work performed.

  - Control all Inspection and Test records and associated Quality related documentation, and the ultimate hand-over to Company as specified in the Coordination Procedures.

  - The Contractor shall support Company's Quality activities related to the Work.

  - The Contractor shall ensure, whenever new technology / concept is introduced the same shall be supported with design and engineering validation.

## QUALITY PROGRAMS, PLANS AND PROCEDURES

### 4.2.1 Project Quality Plan

The Contractor shall implement Contractor's Quality Program or Quality System Manual through a Work-specific Project Quality Plan (PQP)

- The Contractor shall submit the Contractor's Project Quality Plan to the Employer for approval.

- The Quality Plan should be based on existing Quality Management Systems or Programs in use, but shall comply with the requirements listed in the present chapter.

### 4.2.2 Individual Quality Plans

The Contractor shall require Individual Quality Plans, tailored as appropriate for the scope of Work, for the following and shall obtain Employer’s approval of the Plans from:

- Design subcontractors.

- Vendors and Sub-vendors approved by [Company], supplying critical materials and equipment Category I and II criticality as defined by [chapter 4.6 for Category III and IV] only when required by [Company]. This includes shop fabricators and manufactures.

- Construction, installation and commissioning.

### 4.2.3 Ready for Implementation

Quality Plans shall be in place and ready to implement prior to the release of Quality-related Work within the scope of the plan. Ready for implementation shall be defined as follows:

- All comments on the plan have been acceptably resolved and Company approval has been obtained

- Comments have been acceptably resolved on all procedures required to implement the plan. The procedures have been issued within the document control system

- Personnel who shall implement the procedures have received appropriate training or familiarization with the project-specific requirements

### 4.2.4 Control Procedures

The Contractor shall perform Work activities in compliance with Control Procedures and impose a similar requirement on Subcontractors, Vendors, and Sub vendors.

The Contractor shall provide control procedures to reflect the Quality activities of the Job Specification and implement the Project Quality Plan for all phases of the Work. Contractor shall, as far as practical, provide existing procedures that adequately address the controls required for Quality activities. Each Control Procedure shall, at a minimum, include the following elements:

    - Detailed description of how the Work is to be performed, reviews and approvals required, and checks/inspection to be conducted, including responsibilities.

    - Timing of the required checks/inspections in the Work sequence.

    - Accept/reject criteria applicable to the activity and/or approval requirements.

### 4.2.5 Inspection and Test Plans

- The Contractor shall perform inspections and testing in accordance with Inspection and Test Plans (MQP/ITPs).

- The Contractor shall submit MQP/ITPs in compliance with Appendix B to Company for approval prior to start of the Work activity covered by the MQP/ITP. The preferred format is provided in [Appendix B]. The Contractor may adopt any format that conveys the same level of information and addresses the sequencing of the Work. MQP/ITPs may be submitted separately for each discipline.

- Individual MQP/ ITPs for manufacturing, fabrication, construction, installation and commissioning are required for the following:

    - Contractor when Work is performed directly.

    - Vendors and Sub-vendors approved by the Company, supplying critical materials and equipment (Category I, II, III, IV criticality as defined), including shop fabrication and manufacturers.

    - Construction, installation, and subcontractors.

    - Commissioning Team.

- Each plan shall include a list of the specifications that must be met, describe the tests that shall be done to ensure compliance, and identify who shall perform the tests. Further, each such plan shall identify inspections and Quality steps that shall be taken by the Subcontractors, Vendors, and Sub vendors in addition to those done by Contractor or Company.

## SPECIFIC REQUIREMENTS

### 4.3.1 Quality Audit

- The Contractor shall submit Contractor's Quality Audit schedule, including audits of Contractor, Subcontractors, Vendors, and Sub vendors to Company for review and comment.

- The Contractor shall implement and maintain the Quality Audit Schedule to provide periodic verification of compliance with the approved Quality Plans, Inspection and Test Plans, and associated Control Procedures including those of Subcontractors, Vendors, and Sub vendors.

### 4.3.2 Design Control

- Contractor shall perform design control, including establishing design requirements, reviewing design inputs, and reviewing and approving design outputs. Contractor shall develop a matrix identifying Contractor and Company personnel participation in design review and approval.

- Contractor shall control design changes. Maintain design change control log. Include review by Quality Representative for compliance with Quality requirements.

- Contractor shall prepare design review plan and design verification plan. Conduct design reviews and verification, including independent reviews, to ensure that design requirements are met.

### 4.3.3 Inspection and Testing

- Contractor shall identify, segregate, control, track, and certify equipment and materials to be incorporated into the Facility.

- Additionally, Contractor shall ensure that inspection and testing activities conducted during the Work are:

    - In accordance with approved control procedures

    - Conducted at agreed pre-designated stages

    - Coordinated with the Company and/or regulatory authority with adequate (as agreed by Company) notification of nominated hold and witness points requiring their participation

    - Supported by documentation generated to provide objective evidence of acceptable Quality and compliance with Company-specified requirements

- Contractor shall conduct in-process inspection during fabrication, construction, installation and commissioning, mechanical completion, and commissioning, and shall include all disciplines required to complete critical items.

- Contractor shall develop and implement corrective and preventive actions to resolve Quality issues and concerns for all phases of Work. All non-conformances shall be resolved and tracked to closure by Contractor.

- Contractor shall ensure qualified inputs, qualified resources (personnel, tools, equipment, and materials), and qualified Work processes are used to produce Work products in conformance with the Job Specification.

### 4.3.4 Quality Documentation

- Contractor shall track all Quality submittals and maintain a register of status to ensure that submittals are provided and approved in a timely manner.

- Contractor shall demonstrate, when requested, that:

    - All personnel related to a given Work process understand the respective job requirements

    - Qualified inputs are utilized in the Work processes to produce Work products that meet the Job Specification. Quality process inputs include qualified workers, qualified tools, qualified equipment, and qualified materials

    - Work products follow the specified job requirements through inspection and surveillance

- Contractor shall provide Company personnel and designated representatives timely and free access to all Work (materials, equipment, Work Sites, documents, and records) for the purpose of review, inspection, audits, and surveillance. Contractor shall ensure that Subcontractors, Vendors, and Sub vendors are also required to prove this right of access.

### 4.3.5 Criticality

Contractor shall apply Quality verification, surveillance, inspection, and testing commensurate with the importance (criticality) of the Work activity or the equipment or material item:

- Contractor shall develop critical rating system for the procurement of materials and equipment

- Contractor shall obtain Company approval of this system. Contractor shall include the results of the criticality rating of construction, installation, and commissioning activities in the Audit (surveillance) schedule and applicable ITPs

- For listed critical equipment the Contractor shall produce documentary evidence for successful operation of similar capacity rating. The Contractor shall provide necessary documentary evidence of equipment operation at least 2 years in two different power plants.

## Quality Plan Contents

The Quality Plan shall consist of the following:

- Scope and estimated cost of all works on buildings and facilities of the project

- Quality objectives

- Definitions, terms, and abbreviations

- Contractor's organization chart showing all individuals having responsibility for Quality activities and how these individuals are integrated into Contractor's organization responsible for contract Work

- Defined roles and responsibilities for all Quality activities including the roles and responsibilities of Contractor's management

- Idopentification of Contractor's existing procedures which are applicable to the Work

- Identification of Contractor's procedures that are new or existing procedures that were modified to reflect Contract unique requirements

- A description of the following shall be included:

  - How information reports and records relating to Quality assurance and Quality control shall flow among the various groups (e.g., design, engineering, purchasing, construction, controls, other Contractors) and Company and how this information shall be stored and retrieved

  - How procurement documents shall be prepared to properly establish Quality activity requirements with Subcontractors, Vendors, and Sub vendors

  - Contractor's process for determining the type of Quality plan (e.g., Quality Assurance Plan, Quality Control Plan, or Process Control Plan) appropriate to the Scope of Work and requirement for Subcontractors, critical Vendors, and Sub vendors to prepare the product-specific or service-specific Quality plan for their respective scopes of supply

  - How potential Subcontractors, Vendors, and Sub vendors shall be evaluated/selected to ensure they have the requisite resources, tools, procedures, and Quality capabilities to meet established requirements

  - How individual inspection plans shall be prepared for each equipment or material item assigned a Criticality Rating Category of I, II, III or IV

  - How calculations and fabrication drawings prepared by Subcontractors, Vendors, and Sub vendors shall be reviewed for consistency with engineering design and standards

  - How records shall be maintained to demonstrate that all design, materials, equipment, and construction conforms to established requirements and how and in what form the records shall be turned over to Company

  - How nonconformities, concessions, and waivers shall be controlled and resolved including the process that shall be used, the personnel responsible for administering the process, and the information flow through Contractor's organization for resolution

  - How all instruments used for testing and inspection in the Work shall be properly certified equipment for calibrating instrumentation, test gauges and the like. Contractor shall identify the instruments to be certified and describe the methods to be used

  - The auditing, surveillance, appraising, sampling techniques, reviews, and reporting Contractor intends to carry out for the Work to confirm the effectiveness of the Quality activities, and that the Quality Plans and ITPs are complied with

  - The Quality feedback process, to be implemented by each Quality organization (Contractor, Subcontractors, Vendors, and Sub vendors), which requires the Quality organization to inform their client's Quality organization of issues impacting Quality that are not being resolved in a timely manner

  - How Contractor shall implement the requirements of [Appendices B, C, and D] of this specification for the Work

- Contractor's plan for procurement of materials and equipment. Contractor and Company technical and Quality personnel involvement shall be integrated into the plan

- Contractor shall assess the equipment and material to be procured to identify any such items that must be delivered using non-standard shipping or transporting methods or specialized lifting equipment. For such items, a separate Logistics Plan shall be prepared by Contractor and include defined involvement of Contractor and Company personnel

## Purchased Material and Equipment

  - Where practical, all disciplines involved in the Work shall be included in a single ITP

  - A typical ITP format is attached. Each ITP format may vary. However, the following information shall be included in an ITP:

| i. | Activity and associated control procedure(s) and specification(s) reference governing the activity |
| --- | --- |
| ii. | Acceptance Criteria |
| iii. | Responsibility for activity execution |
| iv. | Objective evidence of activity execution or verifying document |
| v. | Contractor/Vendor participation at the inspection and test stages listed |
| vi. | Company participation |
| vii. | Authorized Inspector/CVA participation |

  - ITPs shall, as far as practical, follow the normal sequencing of the Work. ITPs shall identify the stages requiring approval; inspection and testing that include participation by Company, third party, and others, in addition to those inspection stages normally undertaken by Contractor.

  - During Company's review of the Inspection and Test Plans, Company shall identify company-required participation on the Plan.

## Company Criticality Rating System for Procured Materials and Equipment

Obtain Company approval of the criticality rating and designated inspection level.

Category I:

• Contractor need to submit the Quality plan for the equipment and get approval from the Employer / Consultant

• The equipment / materials are subjected to stage inspection by the Employer / Employee representative. Following stages shall be covered

    - Raw Material

    - In Process Inspection

    - Final Inspection

    - Painting

Category II:

• Contractor need to submit the Quality plan for the equipment and get approval from the Employer / Consultant

• The equipment / materials are subjected to final inspection by the Employer / Employer’s representative.

Category III:

• Contractor needs to submit the Quality plan for the equipment and get approval from the Employer

• The equipment / materials are inspected by the Contractor / Contractor’s representative

• Inspection report and material test certificates should be made available for review by the Employer for dispatch clearance

Category IV:

• Contractor needs to submit the Quality plan for the equipment as information to Employer

• The equipment / materials are inspected by the Contractor / Contractor representative

• Inspection and material test certificates should be made available for Employer’s review

## Organizational Responsibilities

Contractor's Quality Organization shall include personnel whose responsibilities, as a minimum, include the activities listed below

Note: It is not the intent of this Appendix to define job titles or the number of individuals the Contractor must hold in their Quality Organization

1. Quality manager, empowered by senior management with operational freedom and authority to manage Quality issues and their resolution, and to oversee the management of Quality project-wide, and to issue stop Work notices as required to correct nonconformance and/or adverse Quality trends

2. Quality auditor(s) to conduct formal internal and external audits on a project-

wide basis throughout the applicable phases of the project execution

3. Quality engineer(s), for design, procurement, construction phases

  - Prepare Quality procedures and plans

  - Conduct reviews of technical specifications for Quality requirements prior to submittal to the Employer for approval

4. Inspection coordinator(s) for procurement, construction phases (inclusive of installation and commissioning) to oversee and implement the approved Contractor Inspection Execution Procedure for Vendor supplied materials and equipment and the daily supervision of Contractor assigned qualified discipline inspectors during construction, installation, and commissioning activities undertaken by Contractor under Contract

5. Inspection supervision to oversee the daily inspection and testing activities associated with construction, installation, and commissioning and the daily supervision of Contractor assigned qualified field discipline inspectors

6. Adequate qualified inspection personnel by discipline to undertake Vendor Inspection activities, conduct surveillance and inspection, witness testing during construction, installation, and commissioning

## Quality Management Coordination Scope

This Appendix establishes Company's Quality assurance/control (QA/QC) requirements to provide assurance that the Work and Facility conform to the Job Specification, regulatory requirements, and sound and generally accepted engineering and construction practices. In this regard, Quality Management is applicable to all Work activities of Contractor, Subcontractor, Vendors, and Sub vendors

4.8.1 Objectives

The objectives of Quality assurance are as follows:

  - Assure installed facilities meet requirements as defined in the Design Basis Memorandum (DBM) and the supporting design and construction specifications, drawings, etc.

  - Assure nonconformance is reported and resolved through approved dispositions and follow-up actions to confirm acceptable results

  - Provide documentation that confirms compliance with project requirements and is sufficient to support production operations

  - Provide early identification of process failures and hardware nonconformance to minimize rework cost and schedule impacts

4.8.2 Contractor Duties

  - Have a documented and functional Quality Management System or Program in place to assure the Quality of the Work. The System or Program shall follow a recognized national or international Quality Standard

  - Assure that the Program or System shall provide an acceptable level of assurance of Quality in Work performance, workmanship, and prevention of nonconformity

  - Comply with this Practice

  - Provide an adequate number of trained and qualified staff to execute the Quality Plan

  - Control the activities of Subcontractors, Vendors, and Sub vendors to ensure compliance with Project Quality requirements

  - Address and resolve, to Company's satisfaction, issues identified during:

    - Company reviews, audits, surveillance, and inspection

    - Third party reviews and inspections

    - Ensure required Quality controlling documents are in place, with all required comments resolved or approved as applicable, prior to allowing any corresponding Work to commence

    - Provide Quality metrics for gauging Quality status and performance, and report status periodically as agreed with Company

4.8.3 Company Duties

Company/BPDB shall perform certain QA/QC activities, the performance of which shall not relieve Contractor of its responsibilities to ensure compliance with the Job Specification or Contractor's overall responsibility for Quality of Work and Facility. Company's Quality activities include:

  - Source Inspection - Company may conduct independent source inspections as the Work progresses. Results of Company source inspections shall be made available to Contractor

  - Design Reviews (both day-to-day review of design documents and Contractor conducted formal design review meetings). During the Work, Company shall perform reviews of design documents. Company's Specialists shall meet with Contractor's engineers periodically to discuss various aspects of the Work. Contractor shall provide the documentation required for Design Reviews and shall follow up on all items not resolved during a review

  - QA Audit - Company shall audit Contractor's QA/QC program. Audit scope shall include, but not be limited to:

    - Review of Contractor's documented QA/QC procedure

    - Random review of Contractor's procurement documents for inspection and specification content

    - Contractor's specific equipment inspection plans in relation to specification requirements and Criticality Rating assessments

    - Review of inspector's surveillance/nonconformance reports

    - Contractor's deviation log and procedure approval logs

    - Receipt inspection discrepancy reports and field inspection reports

    - Activities undertaken by Subcontractors, Vendors, and Sub vendors

  - Approve Contractor, Subcontractor, and critical Vendor/Sub vendor Quality Plans and Inspection and Test Plans prior to start of Work

  - Review and comment on Contractor's Control Procedures and audit schedule, and monitor compliance. Company shall monitor the resolution of any issues raised

  - Participate in design control, including review of design input, and review and approve design output per identified review and approval requirements

  - Approve Equipment Criticality Ratings and Criticality Rating Matrix prior to procurement or provide the Equipment Criticality Ratings

  - Review procurement documents, including changes, for technical and Quality compliance for critical items prior to issue

  - Participate in selected pre-inspection/pre-production meetings

  - Conduct oversight of Contractor's Quality activities, including but not limited to Vendor Inspection activities, Field Inspection, and surveillance activities. Participate in inspection and test stages per approved Inspection and Test Plans (ITPs)

  - Approve Nonconformance Reports (NCRs) where proposed dispositions do not result in meeting the Job Specification

4.8.4 Contractor Interfaces with Company

  - Prepare and submit to Company project-specific Quality Plans that meet the requirements of this procedure

  - Prepare or cause to be prepared Inspection and Test Plans in accordance with this procedure. Obtain Company approval. Company shall annotate the Inspection and Test Plan to indicate items requiring independent Company involvement

  - Prepare or cause to be prepared Control Procedures for Quality-related activities. Obtain Company's determination as to which Control Procedures are to be submitted for review and comment. Obtain Company's comments on required procedures

  - Prepare an audit/surveillance plan covering all Quality-related activities of Contractor, Subcontractors, and critical Vendors and Sub vendors, and obtain Company's review and comment

  - Prepare Criticality Ratings in accordance with this Procedure unless the Criticality Rating has been provided by Company. Obtain Company approval of Contractor- developed Criticality Ratings for equipment

  - Obtain Company's prior approval of dispositions for any nonconforming conditions that do not result in meeting Job Specification, including but not limited to "repair" or "use as is."

# documentation to be provided by the company

- The Contractor must provide the Employer with the manufacturers' name, specification and operating manual for each component of the Facility procured.

- The Contractor is responsible to provide all necessary information, documents, drawings, calculations, schedules, etc. required for the smooth and contractually compliant execution of the work.

- All documentation provided for this project shall be in English language and signed by a relevant registered [Bangladeshi engineer] if required.

- In case that any relevant official documents are not available in English, the Contractor shall be responsible and bear all cost that the relevant documents shall be translated by an Official Authorized Translator into English version. The official translated documents shall be submitted to the Employer/Employer’s Engineer.

- The Employer reserves the right to request additional documentation, if deemed necessary for the execution of the project at any stage.

- The Contractor shall prepare an initial level 4 Project Schedule and keep it updated with the frequency detailed in the Contract.

- Within a maximum of 10 days after the Contract has been awarded, the Contractor shall submit for Employer’s approval, the preliminary list of documentation and the planned submittal dates, in accordance with the Project Schedule.

## PROJECT DOCUMENTATION

All documents in the list below shall be submitted to the Employer’s Engineer prior to the construction and execution. All documents have to be approved twenty-one (21) days before the Contractor is allowed to start the execution.

It is the Contractor’s responsibility that the documentation shall be submitted with sufficient advanced time prior to starting the procurement process. Submitted documents shall be reviewed and commented by the Employer and the Employer’s Engineer. Time for the resubmission of commented and revised documents by Contractor shall not exceed 5 days.

Site suitability

- Geotechnical and soil study

- Topographical study

- Flood risk study

- Other constraints study (road access, livelihood activities, etc.)

Project drawings

- Plant layout and general arrangement

- Cable routing drawings

- Cable list

- Cable schedule/ cable interconnection document

- Single line diagram

- Configuration of strings (string numbers, in order to identify where the strings are in relation to each connection box and inverter)

- Earthing / grounding system layout drawing

- Lightning protection system layout drawing

- Lighting system layout drawing (optional)

- Topographic drawing

- Distribution line plan and elevation

- Substations layout

- Substations shop drawings

Project studies (to be done with PVsyst/Homer Pro)

- Shading study / simulation

- Energy yield study / simulation

- Inverter sizing study

Studies required by Bangladeshi regulation

- Voltage drop calculations

- Protection coordination study

- Short circuit study

- Grounding study

- Cable sizing calculations

- Lightning protection study

PV Panels

- Datasheets

- Flash list with PV modules positioning on the field

- Warranties and certificates

Inverters (Grid Tied & Battery Inverter)

- Inverter cabin foundation drawing

- Inverter layout and general arrangement drawing

- O&M manual

- Commissioning report

- Warranties and certificates

- Factory Acceptance Test

- Inverter settings

- Dimensional drawings

Low Voltage/ACDB

- Low Voltage / ACDB cabin layout and general arrangement drawing

- Low Voltage / ACDB cabin foundation drawing

- LVAC system layout drawing

- LVAC system installation and O&M manual

- Cable list

Cables

- Datasheets

- Type and Routine test reports

Battery Energy Storage System (BESS)

- BESS cabin foundation drawing

- BESS layout and general arrangement dryhn awing

- HVAC (Heating, Ventilation and Air Conditioning) System

- Fire Suppression

Medium Voltage Switchgear/MV Substation

- Single line diagram

- Erection procedure

- Internal normal / emergency lighting layout drawing

- Fire detection and firefighting system layout drawing (if required)

- MVAC system layout drawing

- MVAC system installation and O&M manual

- MV equipment datasheets and manuals (CTs, VTs, circuit breakers, disconnectors, surge arresters, post insulators)

- Protection and metering single line diagram

- Warranties and certificates

UPS and Batteries

- Installation and O&M manual

- Commissioning report

- Warranties and certificates

- Datasheets

- Dimensional drawings

Mounting structures

- Mechanical assembly drawings

- Warranties and certificates

- Structural design calculation (rooftop systems only)

Security, anti-intrusion and alarm system

- Security system layout / general arrangement drawing

- Security system block diagram

- Alarm system schematic diagram

- Equipment manuals and datasheets

- Access to security credentials (e.g. passwords, instructions, keys etc.)

- Warranties and certificates

- Service level agreement with security company (if applicable)

PCMS

- Installation and O&M manual

- List of inputs by type (digital, analog or bus); I/O list includes e.g. sensor readings that are collected by data loggers

- Electrical schematic diagram

- Block diagram (including network addresses)

- Equipment datasheets

Plant control

- Power plant control system description

- BESS control system description

- Control room

- Plant controls instructions

- Breaker control functionality (remote / on-site) and instructions

- List of inputs and outputs

Emergency Generator Set

- Installation and O&M manual

- Commissioning report

- Warranties and certificates

- Datasheets

- Dimensional drawings

Civil Work/Control Room/Office Building

- Civil Construction Drawings

- Building Foundation Drawing

- Structural Design and Drawing

- Floor Plan

- Design Calculations

- Electrical Drawings

- Process & Instrument Diagrams (P&ID)

Distribution Line:

- 11kV Distribution line

- 11/0.4 kV Distribution line

- 0.4 kV Distribution line

## FINAL PROJECT DOCUMENTATION

- The Contractor shall provide comprehensive final project documentation not limited to the documents listed in. The Employer reserves the right to ask for any additional documentation throughout the project. All requested documents for the commissioning of the Plant have to be provided earliest possible before the commissioning. The complete project documentation shall be finally delivered (30 days after Provisional Acceptance).

- IEC 62446 shall be used as a guideline for the final documentation.

- The Contractor shall provide a draft of all documents to the Employer’s Engineer for review before handover the final documentation.

- The final documentation shall be delivered in three (3) hardcopies incl. as-built drawings and two (2) set of soft copies. Softcopies shall be delivered on memory-stick and shall contain *.pdf format files as well as native files. All as-built drawings must be provided in the latest AutoCAD *.dwg and *.pdf files.

## AS-BUILT DRAWINGS

The Contractor shall provide As-Built versions of the entire project documents and drawings listed in.

As-Built drawings and documents will reflect all modifications and changes made during the construction and commissioning phases.

The Contractor’s site staff shall incorporate red-line changes to the approved project drawings. These record drawings shall be reviewed by the Employer’s Engineer. Upon approval and receipt of comments, if any, the Contractor will use these record drawings as the basis for the as-built drawings.

The Contractor shall submit the final As-Built drawings to the Employer’s Engineer for review. The As-Built drawings shall be marked with the changes in relation to the detailed design with notes or comments of all parties, if any. After review and approval, they shall be incorporated into the O&M manuals and shall be filed in a separate as-built drawing book.

## ACCEPTANCE AND CLOSE UNIT REPORT

The Close Out report shall contain the following as a minimum and must be submitted prior to applying for Provisional Acceptance:

- Work Status Report approved by Employer’s Engineer

- Commissioning Report approved by Employer’s Engineer

- Permit & Licenses Status Report

- Employer’s Regulation Compliance Report

- First Synchronization Status

- As-built drawings

- Punch list signed by the Employer and Employer’s Engineer

- List of remaining works signed by the Employer and Employer’s Engineer

- Compilation of all work inspection reports

- All PV and equipment testing reports

- Manufacturer warranties certificates (in the name of the Employer)

- Contact Details of all Manufacturers, Suppliers and Subcontractors

## OPERATION AND MAINTENACE MANUAL

The following outline is a guide to the content of manuals which should be adequately covered in the manual. The Employer shall review the same during detailed engineering stage and final contents shall be agreed upon at that time. The Contractor shall propose the outline of each section:

- Plant Operation & Plant Safety

- Operating and Preventive Maintenance Procedures

- Spare part list including required inventory levels

- Pre-Commissioning and Commissioning Procedures

- Plant Performance Guarantee

- Plant Availability Guarantee

## TRAINING PROGRAM FOR THE EMPLOYER

The Contractor shall propose and conduct Training Programs for the Employer. The training shall include on-site training and off-site training.  The off-site training shall be completed at least six (6) months prior to the start of the commissioning phase of the Plant.  The off-site training shall be conducted in Manufacturers’ premises and/or reputed and competent foreign training institute.  The off-site training should cover at least the operation and maintenance of: (i) solar component (such as PV module, DC combiner box, Grid Tied Inverter, Battery Inverter, weather station, etc.), (ii) transformer, switchgear and substation, and (iii) protection and control system (such as PCMS, relay etc.), (iv) Battery Energy Storage System The costs of the training including travel, accommodation, ground transportation, food and subsistence shall be borne by the Contractor.  In addition, each person will be paid US$ 100 per day as out-of-pocket expenses.

The on-site training prior to O&M phase shall be conducted in the project area or in other suitable places near to the project area.  The on-site training shall be arranged prior to commission of the Plant for about four (4) weeks for detail operation and maintenance of each component/equipment of the Plant.  The training shall certify that the persons obtaining training will be capable to operate and maintenance the plant independently.

The Contractor shall carry out on the job training for the operation and maintenance personnel of the Employer during the defect warranty period.  The training shall be conducted for a period equivalent to one (1) week duration for each quarter and this may not be continuous.

The training program shall cover commissioning including shutdown, emergency, handling upsets and normal operations and maintenance. It shall consist, but not limited to training manual, training methodology, on-job training procedures and syllabus and assessment program. The Contractor shall conduct an assessment soon after completion of each training module. The Employer´s personnel who have passed the assessment shall actively participate in commissioning, operation and maintenance of the Plant.

The bidder shall submit the Training Program with the bid which may consist but not limited to:

The training program and methodology

- Training schedule

- Training methodology

- Training contents

- On-job Training.

- All relevant documentation including Facility-manufacturers’ references, etc.

- Overseas Training

Foreign or overseas Training Venue will be at Manufacturer's Factory Premises. All living, accommodation, food, transport expenses of the trainees/officers during the period of training/study tour including airfares, incidental expenses, medical expenses, medical insurance etc. will be covered by the Contractor including pocket allowance of @ USD 100.00 day/person. The total person-months for training will be limited to 12 (twelve) Person-Months for 14 persons on PV Module, Inverter, BESS, Switchgear, Distribution System and Operation & Maintenance of power plant equipment, orientation & technology transfer at manufacturer's factory

- Training at the Site for O & M

The BPDB shall make available, the Contractor the above-mentioned personnel (total 15 nos.) for the purpose of on-the-job training at site during installation, testing, commissioning and initial operation of the plant for Six (6) man month including Pocket expenses @ BDT 1000 per day per person. All living, accommodation, food, transport expenses of the trainees/officers during the period of training will be covered by the Contractor. During warranty period, it shall be the responsibility of the Contractor to train them adequately and properly in a planned manner so that these members of the Board’s staff could take over the responsibility of operation and maintenance of the plant and equipment independently at the time of handing over of such plant and equipment as well as before issuing of FAC.

Note. Detailed Training Program (including subject, duration, place of training, training methodology, Trainers’ qualification/ experience) shall have to be mentioned by the Tenderer.

# technical document to be included in the technical bid envelope

## Technical Documentation

Aside from the specific information for electrical equipment detailed in chapter 2.11, bidders will include:

Site suitability studies

- Flood risk study

- Other constraints study (road access, livelihood activities, etc.)

Electrical drawings

- Preliminary plant layout and general arrangement

- Single line diagram

- Configuration of strings (string numbers, in order to identify where the strings are in relation to each connection box and inverter)

- Grid access point schematic

- Substation preliminary layout

Civil work documents

- Water management system description (including calculations to justify it will operate as predicted)

- Water management system drawings showing ponds, levelling, drains, and any other element that is the description.

- Access roads for construction, detail of roads and required conservation during construction and operation.

Project studies (to be done with PVsyst/Homer)

- Shading study / simulation

- Energy yield study / simulation

- Inverter sizing study

PV Panels

- Datasheets from preferred suppliers

- Degradation guaranty sheets and certificates

Inverters

- Technical Brochures from preferred suppliers

- Dimensional drawings

- Inverter connection diagram

Distribution Line

- Single Line Diagram (11kV, 11/0.4kV, 0.4kV)

- Pole Fitting Drawing/ Mechanical assembly drawings (11kV, 11/0.4kV, 0.4kV)

- Structural Design Calculation

Cables

- Datasheets from preferred suppliers

MV Switchgear

- Single line diagram

- MV switchyard general arrangement drawing

- MV equipment datasheets and manuals (CTs, VTs, circuit breakers, disconnectors, surge arresters, post insulators)

UPS and Batteries

- Load study

- Technical brochure from preferred suppliers

- Warranties and certificates

Mounting structures

- Mechanical assembly drawings

- Structural design calculation

PCMS

- Equipment datasheets from preferred suppliers

Security system

- General description including number of cameras, detectors, alarms and interconnection to remote monitoring facilities.

## List of Preferred Suppliers

The Contractor shall supply the list of preferred suppliers for the following equipment:

- Solar PV panels.

- Inverters.

- Battery Energy Storage

- Uninterrupted power supply system.

- PCMS software and hardware.

- MV/LV transformers.

- Medium voltage switchgear.

- Low voltage switchgear.

- MV cables.

- LV cables.

- MV equipment.

- DC connectors.

- Security equipment, cameras, detectors, etc.

Any addition to this list of preferred suppliers during project execution must be accepted by the Employer.

No ‘or similar’ items shall be accepted.

: Indicative Single Line Diagram

ANNEX II: Indicative PV Plant Performance

| End of Year | Module degradation Loss in performance | Annual Estimated Production (MWh) | Cumulative Estimated Production (MWh) | Annual Guaranteed Production (MWh) | Cumulative Guaranteed Production (GWh) |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |

This schedule must use the latest radiation and weather data of from Metronome.

- ANNEX III: Guaranteed Annual Performance Schedule

| End of Year | Module degradation Loss in performance | Annual Estimated Production (MWh) | Annual Guaranteed Production (MWh) | Actual Production (MWh) | Annual loss of Production due to curtailment (MWh) |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |

This schedule must use actual radiation and weather data from the Plant’s meteor-stat

- ANNEX IV: Third Party Independent Testing Laboratories/ Institutions

| Sl. No. | Company Name | Sl. No. | Company Name |
| --- | --- | --- | --- |
|  | AIT | 23. | NOA |
|  | Bureau Veritas | 24. | PI Berlin |
|  | Certisolis | 25. | Primara Test-und Zertifizier |
|  | CFV Solar Test Laboratory | 26. | PV Lab Germany |
|  | Chemitox | 27. | PVEL |
|  | CQC | 28. | PVTL |
|  | DEFRA | 29. | Q-Lab |
|  | Digitron Engineering Services | 30. | RETC |
|  | Eliosys | 31. | SGS |
|  | ERDA | 32. | Sky Solar |
|  | Eurofins Product Testing Services (Shanghai) | 33. | Shanghai Ingeer Certification Assessment |
|  | Euortest Laboratori | 34. | Suncycle |
|  | Getecom | 35. | TUV InterCert |
|  | Intertek | 36. | TUV NORD |
|  | JET | 37. | TUV Rheinland |
|  | KACST PVLab | 38. | TUV SUD |
|  | Kiwa Italy SpA | 39. | TUV Thuringen |
|  | Logica | 40. | UL |
|  | MCS | 41. | VDE |
|  | MET | 42. | VDE Global Services Shanghai |
|  | National Technical Systems | 43. | Westpak |
|  | NISE |  |  |

- ANNEX V: Annual Guaranteed Dischargeable Energy & Round-Trip Efficiency

| Year | Minimum Guaranteed Dischargeable Energy (MWh) at 11kV | Guaranteed Dischargeable Energy (MWh) at 11kV | Minimum Round-Trip Efficiency Performance Guarantee at 11kV | Guaranteed Round Trip Efficiency Performance Guarantee at 11kV |
| --- | --- | --- | --- | --- |
| 1 | 16 |  | 90.00% |  |
| 2 |  |  | 90.00% |  |
| 3 |  |  | 88.50% |  |
| 4 |  |  | 88.30% |  |
| 5 |  |  | 88.10% |  |
| 6 |  |  | 87.90% |  |
| 7 |  |  | 87.70% |  |
| 8 |  |  | 87.50% |  |
| 9 |  |  | 87.30% |  |
| 10 |  |  | 87.10% |  |
| 11 |  |  | 86.90% |  |
| 12 |  |  | 86.70% |  |
| 13 |  |  | 86.50% |  |
| 14 |  |  | 86.30% |  |
| 15 |  |  | 86.10% |  |
| 16 |  |  | 85.90% |  |
| 17 |  |  | 85.70% |  |
| 18 |  |  | 85.50% |  |
| 19 |  |  | 85.30% |  |
| 20 |  |  | 85.10% |  |

- ANNEX VI: Guaranteed Components of Distribution System

Components of Distribution System:

| Sl. No. | Item Description | Code1 | Qty. |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |

| Distribution System |  |  |  |
| --- | --- | --- | --- |
| - 11 kV Distribution Line as per BPDB standard (5 KM) |  |  |  |
|  | 12 Meter Steel Pole 350 dan (with anchor block & bottom cover) (in No.). |  | 105 |
|  | 12 Meter Steel Pole 450 dan (with anchor block & bottom cover) (in No.). |  | 35 |
|  | 11 kV Straight Type Cross Arm (in Set). |  | 105 |
|  | 11 kV Tension Type Cross Arm for 3-45 Degree (in Sets) |  | 20 |
|  | 11 kV Tension Type Cross Arm for 46-90 Degree (in Sets). |  | 15 |
|  | 11 kV Pin Insulator with Fittings (in Nos.) |  | 615 |
|  | 11 kV Disc Insulator with Fittings for ACSR DOG (in Set; 1 Set = 2 Nos.) |  | 210 |
|  | 11 kV Guy Insulator (in No.) |  | 75 |
|  | ACSR DOG (in km) |  | 16.5 |
|  | Guy Wire (in km) |  | 1.6 |
|  | Guy Set (in Set) |  | 75 |
|  | Other Line Accessories (in Lot) |  | 1 lot |
| 11/0.4 kV Distribution Line as per BPDB standard (10 KM) |  |  |  |
|  | 12 Meter Steel Pole 350 dan (with anchor block & bottom cover) (in No.). |  | 210 |
|  | 12 Meter Steel Pole 450 dan (with anchor block & bottom cover) (in No.). |  | 70 |
|  | 11 kV Straight Type Cross Arm Set |  | 210 |
|  | 11 kV Tension Type Cross Arm for 3-45 Degree (in Sets). |  | 40 |
|  | 11 kV Tension Type Cross Arm for 46-90 Degree (in Sets). |  | 30 |
|  | 11 kV Pin Insulator with Fittings (in Nos.) |  | 1230 |
|  | 11 kV Disc Insulator with Fittings for ACSR DOG (in Set; 1 Set = 2 Nos.) |  | 420 |
|  | 11 kV Guy Insulator (in No.) |  | 280 |
|  | ACSR DOG (in km) |  | 33 |
|  | Guy Wire (in km) |  | 3.2 |
|  | Guy Set (in Set) |  | 280 |
|  | 5-Spool Wire Rack in set. |  | 350 |
|  | Shackle Insulator (in No.) |  | 2000 |
|  | AAC Wasp (Insulated) (in km). |  | 44 |
|  | AAC Ant (Insulated) (in km). |  | 11 |
|  | Other Line Accessories (in Lot). |  | 1 lot |
| - 0.4 kV Distribution Line as per BPDB standard (15 KM) |  |  |  |
|  | 9 Meter Steel Pole 200 dan (with anchor block & bottom cover) (in No.). |  | 315 |
|  | 9 Meter Steel Pole 300 dan (with anchor block & bottom cover) (in No.). |  | 105 |
|  | 5-Spool Wire Rack in set. |  | 525 |
|  | Shackle Insulator (in No.) |  | 3000 |
|  | 0.4 kV Guy Insulator (in No.) |  | 420 |
|  | AAC Wasp (Insulated) (in km) |  | 66 |
|  | AAC Ant (Insulated) (in km). |  | 16.5 |
|  | Guy wire (in km). |  | 3.75 |
|  | Guy Set (in set) |  | 420 |
|  | Other Line Accessories (in Lot). |  | 1 lot |
| - 11/0.4kV, 250kVA Distribution Transformer (10 Nos) |  |  |  |
|  | 11/0.4 kV, 250 kVA Transformer (in No.) |  | 10 |
|  | 11 kV Lighting Arresters with Fittings (in No.) |  | 30 |
|  | 11 kV DOFC with Fittings (in No.) |  | 30 |
|  | 250A, 3P MCCB with Enclosure Box (in No.) |  | 20 |
|  | PVC Copper Cable 120rm (in meter) |  | 500 |
|  | Transformer Platform (in set.) |  | 10 |
|  | Transformer Earthing (in Nos.) |  | 20 |
|  | Terminal lug, Connector & other accessories |  | Lump Sum |
| - 11/0.4kV, 100kVA Distribution Transformer (15 Nos) |  |  |  |
|  | 11/0.4 kV, 100 kVA Transformer (in No.) |  | 15 |
|  | 11 kV Lighting Arresters with Fittings (in No.) |  | 45 |
|  | 11 kV DOFC with Fittings (in No.) |  | 45 |
|  | 100A, 3P MCCB with Box (in No.) |  | 30 |
|  | PVC Copper Cable 70rm (in meter) |  | 750 |
|  | Transformer Platform (in set.) |  | 15 |
|  | Transformer Earthing (in Nos.) |  | 30 |
|  | Terminal lug, Connector & other accessories |  | Lump Sum |
| - 11/0.4kV, 50kVA Distribution Transformer (20 Nos) |  |  |  |
|  | 11/0.4 kV, 50 kVA Transformer (in No.) |  | 20 |
|  | 11 kV Lighting Arresters with Fittings (in No.) |  | 60 |
|  | 11 kV DOFC with Fittings (in No.) |  | 60 |
|  | 100A, 3P MCCB with Box (in No.) |  | 40 |
|  | PVC Copper Cable 35 rm (in meter) |  | 1000 |
|  | Transformer Platform (in set.) |  | 20 |
|  | Transformer Earthing (in Nos.) |  | 40 |
|  | Terminal lug, Connector & other accessories |  | Lump Sum |
| - 6.35/0.23kV, 10kVA 1P Distribution Transformer (30 Nos) |  |  |  |
|  | 6.35/0.4 kV, 10 kVA 1P Transformer (in No.) |  | 30 |
|  | 11 kV Lighting Arresters with Fittings (in No.) |  | 30 |
|  | 11 kV DOFC with Fittings (in No.) |  | 30 |
|  | 50 A 1P MCCB with Box (in No.) |  | 30 |
|  | PVC Copper Cable 25rm (in meter) |  | 600 |
|  | Clamp for Transformer and Side Mount Bracket for LA & DOFC (in set.) |  | 30 |
|  | Transformer Earthing (in Nos.) |  | 30 |
|  | Terminal lug, Connector & other accessories |  | Lump Sum |

Service Wire and Metering Arrangement for End Mile Connection as per BPDB standard:

| Sl. No. | Item Description | Code1 | Qty. |
| --- | --- | --- | --- |
| (1) | (2) | (3) | (4) |
| Service Wire and Metering Arrangement for End Mile Connection as per BPDB standard |  |  |  |

| LT/MT/HT Consumer: Single Phase Meter (Nos) & Three Phase Meter (Nos) |  |  |  |
| --- | --- | --- | --- |
|  | Single Phase Meter (Nos) |  | 1716 |
|  | Three Phase Meter (Nos) |  | 82 |
|  | HT Meter (Nos.) |  | 2 |
| Service Wire |  |  |  |
|  | 4 RM Duplex Service drop Wire (km) |  | 62 |
|  | 6 RM Quadruplex Service drop Wire(km) |  | 12 |
|  | 16 RM Quadruplex Service drop Wire (m) |  | 200 |
|  | 3x70 RM XLPE Cu Cable for HT Consumer (m) |  | 500 |

1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.

NOTE: "Service Wire and Metering Arrangement for End Mile Connection should comply with BPDB standards. Before the installation of single-phase or three-phase meters, the contractor must deposit the required amount with the concerned BPDB office, as per BPDB's Commercial Operation Procedure."

ANNEX VII: TECHNICAL ORIENTATION AND QUALITY TEST WITNESS FOR ALL DISTRIBUTION ITEMS:

A. FACTORY INSPECTION AND TEST WITNESS:

The BPDB’s inspection team proposed by the consignee and approved by the competent authority shall have the right to inspect, examine and test the workmanship and performance of the goods/materials to confirm the conformity to the specification at all reasonable time before and during manufacture at the manufacturer's premises. The team may inspect the goods during the manufacturing process and may also request for the purchase/ import/ shipping documents of raw material (if required) and check those in accordance with Guaranteed Technical Particulars (GTP).

BPDB's Inspection Team will witness the routine test at the manufacturer's premises. Tests shall be performed in accordance with the relevant IEC/BS/ANSI/ASTM/BDS standards or any other standard mentioned in the contract document which shall be complied with the Guaranteed Technical Particulars (GTP) of the Contract. All expenses for such tests shall be borne by the Contractor.

At the time of Factory Test witness BPDB's Inspection Team will check the calibration seal/certificate of the testing/measuring equipment, meters etc. issued by the competent authority. The contractor shall ensure that the Manufacturer shall complete the calibration of the testing/ measuring equipment, meters etc. before the inspection of BPDB's team.

The Supplier shall, after consulting the consignee, give notice to the consignee in writing of the date and the place where the material or equipment will be ready for testing at least 15 days before schedule of inspection. The consignee shall give the supplier timely notice in writing of his intention to attend the test. As and when the consignee is satisfied that any materials/equipment shall have passed the tests referred to in this clause, consignee shall notify the contractor in writing to that effect.

Should any inspected/ tested goods fail to conform to the specification, the consignee shall have the right to reject any of the items or complete batch if necessary. In that case, Supplier has to replace the equipment/goods and to make them according to specification and the supplier shall conduct similar pre-delivery Inspection and factory tests without any financial involvement to the consignee. In case any of the equipment/goods found not conforming to the specification at the time of Inspection, the supplier will in no way be relieved from the responsibility of replacing them on making them according to specification at their own cost, despite the equipment/goods were found according to specification at the time of Factory Acceptance Test in respect of quality and quantity. Nothing in this clause shall in any way release the supplier from any warranty or other obligations under the contract.

If the offered goods are manufactured within the purchaser’s country then the manufacturer/supplier shall have the testing facilities at manufacturer's/supplier's premises in accordance with the relevant IEC/BS/ANSI/ASTM/BDS Standards. The inspector(s) shall sent the sample material (selected by the Engineering Team) to CERS, BPDB/BUET/CUET/KUET/RUET/DUET to carry out any test(s) pending due to lack of testing facilities at the manufacturer's/supplier's premises. All cost of testing including carrying, loading, un-loading etc. will be borne by the supplier and shall be deemed to be included in the offered price. If the sample(s) fails to confirm the specification, the full consignment will be rejected.

No goods shall be packed, prepared for shipment/delivery unless it has been approved and written instructions have been received from the consignee.

On successful completion of Pre-shipment inspection/quality test witness, delivery of goods will be made to the designated stores under contractor’s/supplier’s responsibility until Inspection at site is successfully completed without any obligation on part of BPDB. Quality and quantity of the delivered goods will be determined at the time of Inspection at site at the designated stores in presence of the authorized representative of the contractor/supplier. After approval of the satisfactory Inspection at site, R&I Report will be issued following the contractual obligations.

B. INSPECTION AT SITE:

The Supplier shall inform the consignee immediately after arrival of the goods at the designated store of BPDB (as per delivery schedule). An Inspection team of BPDB (may be the previously or newly formed team) shall start to perform the inspection not beyond 21 (twenty-one) days in presence of supplier's representative. The Supplier shall arrange inspection as per program in consultation with the consignee. If any defect or damage has been found at inspection, the defective or damaged materials/ goods shall be replaced by the supplier at his own cost within the stipulated time.

The consignee's right to inspect, test and reject the goods after delivery at the designated stores of BPDB shall in no way be limited or waived by reason of the goods having previously been inspected, tested and passed by the purchaser prior to the goods' delivery.

The Inspection team will check the physical conditions and quantity of the goods delivered. If necessary the inspection team will select the sample of good(s) on random sampling basis and sent the selected sample goods to CERS, BPDB or BUET/ CUET/ KUET /RUET/DUET (as selected by the inspection team) to carry-out the test(s) as per contract to confirm the conformity to the approved Technical Specifications, Guaranteed Technical Particulars (GTP), drawings and relevant standards. If the tested sample(s) fail to confirm the specifications in tests, the full consignment will be rejected. All cost of testing of Materials/ Goods including carrying, loading, un-loading etc. will be borne by the supplier

ANNEX VIII: Technical Specifications/ Requirements of

Double cabin Diesel Pick Up

General

This section of the document includes the design, manufacture, testing & inspection of Double cabin Diesel pick up as specified.

# Climate Data

The equipments to be supplied against this contract shall be suitable for satisfactory use under the following climatic condition:

| Climate | : | Tropical, intense sunshine, heavy rain, humid. Maximum Humidity and Temperature sometimes occur simultaneously. |
| --- | --- | --- |
| Maximum Temperature | : | 400 C |
| Minimum Temperature | : | 030 C |
| Maximum yearly weighted average temperature | : | 300 C |
| Relative Humidity | : | 50-100% |
| Annual Mean Relative Humidity | : | 75% |
| Average isokeraunic level | : | 80 days/ year |
| Average annual rain fall | : | 3454 mm |
| Maximum wind velocity | : | 200 km/ hour |
| Maximum Altitude above the sea level | : | 300 metres |
| Atmospherically, Mechanical and Chemical impurities | : | Moderately polluted |

Vehicles as specified will be used in tropical locations and in a hot humid environment with presence of the insects and vermin.  The information is given as a guide for Tenderer and no responsibility for its accuracy will be accepted, nor will any claim based on the above be entertained.

Specifications

| 1.0 | General | : |  |
| --- | --- | --- | --- |
| 1.1 | Type | : | Double Cabin Diesel Pick Up |
| 1.2 | Model | : | 2024/Latest |
| 1.3 | Condition | : | Brand New |
| 2.0 | Body |  |  |
| 2.1 | Number of doors | : | 4 (Four) |
| 2.2 | Seating Capacity | : | 5 Seated |
| 2.3 | Color | : | Manufacturer's standard color |
| 2.4 | Drive | : | Right hand drive |
| 2.5 | Top | : | Hard Top (Metal) |
| 3.0 | Engine |  |  |
| 3.1 | Combustion system | : | 4- Stroke, 4- cylinder, in line |
| 3.2 | Fuel | : | Diesel |
| 3.3 | Fuel tank | : | 80 Litre (Minimum) |
| 3.4 | Displacement (CC) | : | 2700 (Minimum) |
| 4.0 | Transmission system |  |  |
| 4.1 | Transmission | : | Part time manual 4x4 |
| 4.2 | Gearbox | : | Automatic |
| 4.3 | Rear differential | : | Manual locking |
| 5.0 | Steering System | : | Power |
| 6.0 | Brake System |  |  |
| 6.1 | Front brake | : | Ventilated discs |
| 6.2 | Rear brake | : | Drums |
| 6.3 | Parking brake | : | Manual |
| 7.0 | Suspension system |  |  |
| 7.1 | Front suspension | : | Coil type |
| 7.2 | Rear suspension | : | Leaf |
| 8.0 | ## Tyre and Wheel |  |  |
| 8.1 | Tyre dimension | : | 265/65 R17 |
| 8.2 | Wheels | : | Aluminium GR-S |
| 8.3 | Spare wheel | : | Aluminium GR-S |
| 9.0 | Battery Volt | : | 12 Volt, 65 Ah (Min) |
| 10.0 | Built-in equipment & accessories | : | Driver & Passenger Airbags, ABS, Anti-theft alarm, Front & Rear Headrests, Front Mud Guard, Rear Mud Guard, Clear Laminated Windshield & Tampered Window Glasses, Power windows (Front , Rear), Black Windshield Moldings, Headlamps (LED), Fixed Intermittent multi speed Windshield Wiper & Washers, Black GR-S design Front grill, Stainless Steel Front & Rear Bumper, Mud Grip type tires with one spare Wheel, Clear Rear Window Glass, Black Door Mirrors (Electric Adjustable Side view mirrors), Rear View Mirrors, Sun Shed 2 pcs, Floor Mat, Side step, Black Outer Door Handle, Power Steering , Height and reach adjustable steering wheel (Leather), Steering wheel audio control, Steering Wheel Lock, Push & start system, Smart keys, Front and Rear Seat belt, Seatbelt warning, Central door locking while driving, Door unlock alert, Height and reach adjustable Driver seat, Radio MP3, Touchscreen Player (USB , Bluetooth, Apple CarPlay , Android Auto), Panoramic view monitor (360°) Camera, Front / Rear Parking sensor, Front Fog lamps, Built-in climate control system, Ventilator, Fuel/Lube oil /Speedometer, Cigarette Lighter etc. |
| 11.0 | Type of AC included | : | Automatic driver & passenger |
| 12.0 | Repair Tools | : | Manufacturer's standard Tools with Jack including handle and Wheel Wrenches |
| 13.0 | Spares | : | Manufacturer's standard Spares With one spare Wheel, Maintenance & Repair Manual. |
| 14.0 | Canopy | : | Canopy to be fitted by the supplier within the quoted price as per instruction by the consignee. |
| 15.0 | Registration | : | Registration to be done by the supplier within the quoted price as per instruction by the consignee. |

Features & Accessories

The Double Cabin Diesel Pick-up to be supplied under this contract shall have to be equipped with the following equipment:

-	The components list, operating instructions, maintenance manual, manufacturer’s catalogue etc. to   be supplied with each unit.

- The detail technical specification including dimensions, weight, manufacturer’s name, model, catalogue reference no. etc. with all necessary accessories to be provided with each unit.

ANNEX IX: Technical Specifications/ Requirements of

Electric Vehicle

General

This section of the document includes the design, manufacture, testing & inspection of Electric Vehicle as specified.

# Climate Data

The equipment to be supplied against this contract shall be suitable for satisfactory use under the following climatic condition:

| Climate | : | Tropical, intense sunshine, heavy rain, humid. Maximum Humidity and Temperature sometimes occur simultaneously. |
| --- | --- | --- |
| Maximum Temperature | : | 600 C |
| Minimum Temperature | : | -300 C |
| Maximum yearly weighted average temperature | : | 300 C |
| Relative Humidity | : | 50-100% |
| Annual Mean Relative Humidity | : | 75% |
| Average isokeraunic level | : | 80 days/ year |
| Average annual rain fall | : | 3454 mm |
| Maximum wind velocity | : | 200 km/ hour |
| Maximum Altitude above the sea level | : | 300 metres |
| Atmospherical, Mechanical and Chemical impurities | : | Moderately polluted |

Vehicles as specified will be used in tropical locations and in a hot humid environment with presence of the insects and vermin.  The information is given as a guide for Tenderer and no responsibility for its accuracy will be accepted, nor will any claim based on the above be entertained.

Specifications

| 1.0 | General | : |  |
| --- | --- | --- | --- |
| 1.1 | Type | : | Electric Vehicle |
| 1.2 | Model | : | 2024/Latest |
| 1.3 | Condition | : | Brand New |
| 2.0 | Body |  |  |
| 2.1 | Number of doors | : | 4 (Four) |
| 2.2 | Seating Capacity | : | 5 Seated |
| 2.3 | Color | : | Manufacturer's standard color |
| 2.4 | Drive | : | Right hand drive |
| 2.5 | Top | : | Hard Top (Metal) |
| 3.0 | Electric Motor |  |  |
| 3.1 | Motor type | : | Permanent magnet synchronous motor |
| 3.2 | Power (kW) | : | 100 (Maximum) |
| 3.3 | Torque (N.m) | : | 300 (Maximum) |
| 4.0 | Performance |  |  |
| 4.1 | Acceleration 0-100km/h (s) | : | 11 (Maximum) |
| 4.2 | Driving range: WLTP-Combined (km) | : | 340 (Minimum) |
| 5.0 | Battery |  |  |
| 5.1 | Battery type | : | Blade Battery |
| 5.2 | Battery capacity (kWh) | : | 49.50 (Minimum) |
| 6.0 | Brake |  |  |
| 6.1 | Front | : | Ventilated Disc |
| 6.2 | Rear | : | Disc |
| 7.0 | Suspension system |  |  |
| 7.1 | Front suspension | : | Macpherson Strut |
| 7.2 | Rear suspension | : | Multi-link |
| 8.0 | ## Tyre and Wheel |  |  |
| 8.1 | Tyre Size | : | 215/60 R17 (Minimum) |
| 8.2 | Wheel type | : | Alloy |
| 9.0 | Built-in equipment & accessories | : | Portable Charging Cable (mode-2), AC Charging Port- Type 2, DC Charging Port CCS 2, V2L Function, V2L Discharge Adapter, Regenerative Braking, Sunroof, Electric Unlock Tailgate, Roof Rails, Electrically Heated, Adjustable and Retractable Exterior Mirrors, Steering Wheel Mounted Control, Electric Power Steering System, 5” digital Instrument Panel, Synthetic leather seat, Adjustable Driver and Passenger Seat, Front and Side Airbags, Side Curtain Airbags, Far-side Airbag, Tyre Pressure Monitoring System, Electric Paring Brake System, ABS, Automatic Emergency Braking System, Collison Warning, LED Headlight and Rear Light, Follow me Home Headlight, 360ᵒ View Monitor, Anti-theft alarm, Front & Rear Headrests, Front & Rear Mud Guard, Clear Laminated Windshield & Tampered Window Glasses, Power windows (Front , Rear), Multi speed Windshield Wiper & Washers, Stainless Steel Front & Rear Bumper, Black Door Mirrors, Rear View Mirrors, Sun Shed 2 pcs, Floor Mat, FM Radio, Bluetooth Connectivity, 15” (minimum) Intelligent Rotating Touch Screen, USB-C Port and USB-A Port for Centre and Rear Console, Wireless Phone Charger, Portable Card Key, Tyre Repair Kit, Automatic Air-Conditioning, CN95 Air Filter, Front and Rear Seat belt, Seatbelt Reminder, Central door locking while driving, Door unlock alert etc. |
| 10.0 | Type of AC included | : | Automatic Air-Conditioning (Front-Rear) |
| 11.0 | Repair Tools | : | Manufacturer's standard Tools |
| 12.0 | Spares | : | Tire repair kit with inflator machine provided by the manufacturer |
| 13.0 | Registration | : | Registration to be done by the supplier within the quoted price as per instruction by the consignee. |

Note:    The Blade Battery shall use Lithium Iron Phosphate (LFP) technology and shall be designed for high safety, long cycle life, and stable performance. The battery shall be rated for approximately 3,000 charge cycles, with an estimated lifespan of years (depending on usage conditions). It should support both AC and DC fast charging, with DC fast charging enabling an 80% charge in approximately 30–45 minutes under optimal conditions.

Features & Accessories

The Electric Vehicle to be supplied under this contract shall have to be equipped with the following equipments:

-	The components list, operating instructions, maintenance manual, manufacturer’s catalogue etc. to   be supplied with each unit.

- The detail technical specification including dimensions, weight, manufacturer’s name, model, catalogue reference no. etc. with all necessary accessories to be provided with each unit.

ABBREVIATIONS

AASHTO	American Association of State Highway and Transportation Officials

AC	Alternating Current

ACI	American Concrete Institute

AISC	Code of Standard Practice for Steel Buildings and Bridges

ASTM	American Institute of Steel Construction

BNBC	Bangladesh National Building Code

BOS	Balance of System

BREB	Bangladesh Rural Electrification Board

CBR	California Bearing Ratio

CCTV	Closed Circuit Television

db	decibel

EGCB	Energy Generation Company of Bangladesh

GoB	Government of Bangladesh

DC	Continuous Current

DoF	Department of Fisheries

EGCB	Electricity Generation Company of Bangladesh

ERP	Enterprise Resource Planning

FGL	Finished Ground Level

FM	Fineness Modulus

GI	Galvanized Iron

GIEE	Guideline for Installation of Electrical Equipment

GEPaD	Good Engineering Practice and Design

HV	High Voltage

Hz	Hertz

IEC	International Electrotechnical Commission

IEEE	Institute of Electrical and Electronic Engineers

IFC	International Financial Corporation (World Bank Group)

ITP	Independent Third Party

I/V	Intensity / Voltage

Kg	Kilograms

kV	Kilovolt

kVA	Kilo Volt Ampere

kW	Kilowatt

LED	Light Emitting Diode

LGED	Local Government Engineering Department, Bangladesh

LV	Low Voltage

m.	Meters

mm	Millimeter

MPPT	Maximum Power Point Tracking

ms	millisecond

MV	Medium Voltage

MVA	Mega Volt Ampere

MW	Megawatt

MWh	Megawatt hour

NFPA	National Fire Protection Association

O&M	Operations and Maintenance

PBS	Palli Biddyut Samity

PCMS	Plant Control and Monitoring System

PID	Potential Induced Degradation

PGCB	Power Grid Company of Bangladesh Limited

PV	Photovoltaic

PWD	Public Works Datum

RAP	Resettlement Action Plan

RCC	Roller-Compacted Concrete

RTP	Real-Time Kinetic

SPT	Standard Penetration Test

STC	Standard Test Conditions

TMY	Typical Meteorological Year

TRV	Transient Recovery Voltage

WBM	Water Bound Macadam

XLPE	Cross-Linked Polyethylene

For example, if there is a single transformer, the capacity may reduce by 100% on transformer failure; if there are two inverters, capacity may reduce by 50% on inverter failure; if there are 30 battery modules, performance may reduce by 20% on failure of one battery module.