BANGLADESH POWER DEVELOPMENT BOARD

TENDER DOCUMENT

FOR

CONSTRUCTION OF 50MWp (DC) SOLAR PHOTOVOLTAIC GRID TIED POWER PLANT AT RANGUNIA, CHATTAGRAM, BANGLADESH ON TURNKEY BASIS

(One Stage Two Envelope Tendering Method)

(Design, Engineering, Manufacturing, Supply, Installation, Testing & Commissioning and 2 (Two) Years Warranty Period)

Invitation for Tender No: 27.11.0000.101.14.013.26-937, Dated: 20/04/2026

Schedule and Technical Data Sheet

Volume 2 of 2 (Part B) of the Bidding Document

Secretary

Bangladesh Power Development Board

Wapda Building (1st Floor), Motijheel, C/A.

Dhaka, Bangladesh

April, 2026

1. Schedule A: Guarantees

This schedule shall use the latest site-specific radiation and weather data from Meteonorm for all calculations of Net Plant Capacity, Net Energy Output, and Performance Ratio (PR). All modelling, simulations, and guarantees must be based on this data to ensure accurate and realistic performance assessment.

The bidder shall provide the following guarantees in accordance with the tender requirements; failing which, the bid shall be deemed non-responsive:

1.1 Net Plant Capacity (at high tension side of 33 kV step-up transformer)

- Minimum ________MWac

1.2 Net Energy Output (at high tension side of 33 kV step-up transformer)

- 1st Year: Minimum ___________million kWh

- 2nd Year: Minimum _________million kWh

1.3 PV Module Degradation Guarantee

- 1st Year: Maximum ______%

- 2nd Year to 30th years: Maximum ______% per year

1.4 Time for completion

Total time from effective date to Successful Completion (OAC) of the Plant	: ……………………Days

1.5 Design Life of the Plant

- Minimum _______Years,

1.6 Guaranteed Bid Performance Ratio

For the simulation of the expected yield of the PV plant, which is the basis for the guaranteed performance. The Tenderer is required to perform the yield estimation by using PVsyst software only. The Performance Ratio (PR) of the Power Plant shall be not less than 78% for each calendar month, irrespective of the month of commissioning.

Table: Guaranteed Performance Ratio [PR]

| Month | Performance Ratio (PR) % at Operational Acceptance | 1st Year (during DLP) | 2nd Year (during DLP) |
| --- | --- | --- | --- |
|  |  | Performance Ratio (PR) % | Performance Ratio (PR) % |
| January |  |  |  |
| February |  |  |  |
| March |  |  |  |
| April |  |  |  |
| May |  |  |  |
| June |  |  |  |
| July |  |  |  |
| August |  |  |  |
| September |  |  |  |
| October |  |  |  |
| November |  |  |  |
| December |  |  |  |
| Mean PR |  |  |  |

- 1.7 Guaranteed Bid Performance Schedule

| End of Year | Module degradation Loss in performance | Annual Estimated Production (MWh) | Cumulative Estimated Production (MWh) | Annual Guaranteed Production (MWh) | Cumulative Guaranteed Production (GWh) |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |
| 21 |  |  |  |  |  |
| 22 |  |  |  |  |  |
| 23 |  |  |  |  |  |
| 24 |  |  |  |  |  |
| 25 |  |  |  |  |  |

This schedule shall be based on the latest site-specific radiation and meteorological data from Meteonorm used in the PVsyst model submitted with the Bid.

1.8 Guaranteed Annual Performance Schedule

| End of Year | Module degradation Loss in performance | Annual Estimated Production (MWh) | Annual Guaranteed Production (MWh) | Actual Production (MWh) | Annual loss of Production due to curtailment (MWh) |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |
| 21 |  |  |  |  |  |
| 22 |  |  |  |  |  |
| 23 |  |  |  |  |  |
| 24 |  |  |  |  |  |
| 25 |  |  |  |  |  |

This schedule shall be filled after Operational Acceptance of the Plant and shall be based on actual radiation and weather data recorded from the Plant’s meteorological (meteo) stations.

1.9 Loss of Production due to curtailment (MWh)

| End of Year | Grid Outage Time (hour) | Daily loss of Production |
| --- | --- | --- |
|  | (Time: 6:00 AM up to 6:00 PM from Mar to Oct and from 7:00 AM up to 5:00 PM from Nov to Feb) | Capacity (AC] × Plant Factor (0.20) × Grid Outage Time (Million kWh) |
| 1 |  |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| . |  |  |
| . |  |  |
| . |  |  |
| 23 |  |  |
| 24 |  |  |
| 25 |  |  |
| 26 |  |  |
| 27 |  |  |
| 28 |  |  |
| 29 |  |  |
| 30 |  |  |
| Total |  |  |

This schedule shall be filled after Operational Acceptance of the Plant

1.10 Annual Loss of Production due to curtailment (MWh)

| End of Month | Monthly loss of Production | End of Year | Annual loss of Production |
| --- | --- | --- | --- |
| 1 |  | 1 |  |
| 2 |  | 2 |  |
| 3 |  | 3 |  |
| 4 |  | 4 |  |
| 5 |  | 5 |  |
| 6 |  | 6 |  |
| 7 |  | 7 |  |
| 8 |  | 8 |  |
| 9 |  | 9 |  |
| 10 |  | 10 |  |
| 11 |  | 11 |  |
| 12 |  | 12 |  |
| 13 |  | 13 |  |
| 14 |  | 14 |  |
| 15 |  | 15 |  |
| 16 |  | 16 |  |
| 17 |  | 17 |  |
| 18 |  | 18 |  |
| 19 |  | 19 |  |
| 20 |  | 20 |  |
| 21 |  | 21 |  |
| 22 |  | 22 |  |
| 23 |  | 23 |  |
| 24 |  | 24 |  |
| 25 |  | 25 |  |
| Total |  |  |  |

This schedule shall be filled after Operational Acceptance of the Plant

2. Schedule B: Technical Data Sheet

The following GTP to be filled up appropriately, then Seal & Signed by both manufacturer and bidder on Manufacturer’s Letterhead Pad. Otherwise, his bid shall be non-responsive.

2.1: Solar Photovoltaic Module

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Description of the Item | Solar PV Module |  |
| 2 | Name of the Manufacturer | To be mentioned |  |
| 3 | Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | IEC61215:2021/IEC61730:2023/IEC61701 / IEC62716 / IEC60068/IEC62804/ISO9001:2015/ISO14001:2015/ISO45001:2018 |  |
| 5 | Model number | To be mentioned |  |
| 6 | Type of solar Cells | N-Type Mono Crystalline Bifacial |  |
| 7 | Rated Power (Pmax) | Minimum 650 Wp at STC |  |
|  |  | Minimum 730 Wp at BNPI |  |
| 8 | Bifacial Factor | Minimum 85 ± 5% |  |
| 9 | Power Tolerance (STC) | 0~+3% |  |
| 10 | Voltage at Pmax (V mp) | To be mentioned |  |
| 11 | Open circuit voltage (Voc) | To be mentioned |  |
| 12 | Bifacial Factor | Minimum 85±5% |  |
| 13 | Temperature Co-efficient (Pmax) | Maximum -0.26%/ºC |  |
| 14 | Temperature Co-efficient (Voc) | Maximum -0.25%/ºC |  |
| 15 | Module Efficiency | Minimum 24.00% |  |
| 16 | Front Glass | 2.00 mm, Anti-Reflection Coating |  |
| 17 | Back Glass | 2.0 mm, Heat Strengthened Glass |  |
| 18 | Frame | Anodized Aluminum Alloy |  |
| 19 | Operating Temperature | Minimum -40ºC to +70ºC |  |
| 20 | Minimum Static Load front and back (e.g. wind) | Front 5400Pascal Rear 2400Pascal |  |
| 21 | Junction Box | IP 68 rated |  |
| 23 | Wind velocity withstands | 200 km/h |  |
| 26 | Annual Degradation | 1st Year: Maximum 1% |  |
|  |  | From 2 - 30 Year: Maximum 0.35% |  |
| 27 | Performance Warranty | Minimum 30 years |  |
| 28 | Product Warranty | Minimum 12 years |  |
| 29 | Certifications | UL, TUV, ISO or equivalent |  |
| 30 | Catalogue | To be submitted |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.2: Grid Tied Inverter

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Name of the Item | Grid Tied Inverter |  |
| 2 | Name of the Manufacturer | To be mentioned |  |
| 3 | Address of the Manufacturer | To be mentioned |  |
| 4 | Standard | IEC 62109-1/-2, IEC 62920, IEC 60947-2, EN 50549-2, IEC 61683 |  |
| 5 | Certifications | To be mentioned |  |
| 6 | Model number | To be mentioned |  |
| INPUT |  |  |  |
| 7 | Max Input Voltage | 1500 V |  |
|  | Startup Voltage | To be mentioned |  |
|  | Minimum No of Independent MPP input | 6 Nos |  |
| OUTPUT |  |  |  |
| 8 | Nominal AC Output Power | Minimum 300kW (at unity PF) |  |
|  | Nominal Output Voltage | 0.8 kV or above |  |
|  | AC Frequency, adjustable | 50 ± 5% Hz |  |
|  | AC Grid Connection | 3 phase, 4 wire |  |
| 9 | Idle power | ≤ 6W |  |
| 10 | Total Harmonic Distortion | < 3% |  |
| 11 | European efficiency | Minimum 98% |  |
| 12 | Power Factor | 0.8 leading to 0.8 lagging |  |
| 13 | Reverse Current Protection | To be incorporated |  |
| 14 | DC Reverse Polarity Protection | To be incorporated |  |
| 15 | Anti-Islanding Protection | To be incorporated |  |
| 16 | Ground Fault Monitoring | To be incorporated |  |
| 17 | Degree of Protection | IP66 |  |
| 18 | Communication | RS485 |  |
| 19 | Display monitor | LED. WLAN+APP or Bluetooth+APP |  |
| 20 | Topology | Transformerless |  |
| 21 | Warranty | Minimum 5 years |  |
| 22 | Catalogue | To be submitted |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.3: Power Transformer

| Sl. No. | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1 | Description of the Item | LV/33 kV, ---- kVA Power Transformer |  |
| 2 | Manufacturer’s Name | To be mentioned |  |
| 3 | Country of the Origin | To be mentioned |  |
| 4 | Manufacturer’s Type/ Model No. | To be mentioned |  |
| 5 | Installation | Outdoor, Tropical, High Rainfall & Humidity |  |
| 6 | Type | Core |  |
| 7 | Coolant | Mineral oil |  |
| 8 | Method of Cooling | ONAN |  |
| 9 | kVA Rating | To be mentioned |  |
| 10 | Number of Phases | 3 |  |
| 11 | Rated frequency, Hz | 50 |  |
| 12 | Rated primary voltage, V | To be mentioned |  |
| 13 | Rated no load sec. Voltage, kV | 33 |  |
| 14 | Vector group | Dyn11 |  |
| 15 | Highest system voltage of- |  |  |
|  | a) Primary winding, V | To be mentioned |  |
|  | b) Secondary winding, kV | 36 |  |
| 16 | Basic insulation level, KV | 170 kV Peak |  |
| 17 | Power frequency withstand voltage, kV |  |  |
|  | a) HT Side | 78 |  |
|  | b) LT Side | 2.5 |  |
| 18 | Relay Protection | 50/51, 50N/51N, 87T (64REF), 24, 59, 27, 67, 67N, with self-protection (Buchholz, PRD, OTI, WTI etc) |  |
| 19 | No-Load Loss (W) | To be mentioned |  |
| 20 | Full Load Loss (W) | To be mentioned |  |
| 21 | Percentage Impedence | 4.5% |  |
| 22 | Catalogue | To be submitted |  |
| H.T WINDING |  |  |  |
| 1 | Nominal Rated voltage | 33 KV |  |
| 2 | Maximum system voltage | 36 KV |  |
| 3 | Basic insulation level (minimum) | 170 kV Peak |  |
| 4 | Tap Changer | +2x2.5%, 0, -2x2.5% of rated kV & all fully rated capacity. Tap Changer shall be off load type |  |
| 5 | Inter phase connection | Delta |  |
| 6 | Bushings | Porcelain, outdoors type with arcing horns of standard gap, mounted on top of tank. Quantity-3 Nos. |  |
| 7 | Power frequency withstand voltage for one minute | 70 kV |  |
| L.T WINDING: |  |  |  |
| 1 | Nominal Rated voltage | To be mentioned (in accordance with the inverter output voltage) |  |
| 2 | Highest system voltage | To be mentioned |  |
| 3 | Basic insulation level (minimum) | To be mentioned |  |
| 4 | Inter phase connection | Wye |  |
| 5 | Bushings | Porcelain, outdoors type with arcing horns of standard gap, mounted on top of tank. Quantity-3 Nos. |  |
| 6 | Power frequency withstand voltage for one minute | To be mentioned |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.4: Switchgear, Control & Protection Panel (630A)

| Sl No | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1. | Description of the Item | MV Switchgear and Metering Panel |  |
| 2. | Standard | Relevant ANSI / IEC Standard |  |
| 3. | System nominal voltage kV | 33 |  |
| 4. | Maximum System Voltage, kV | 36 |  |
| 5. | Rated Frequency Hz | 50 |  |
| A | Vacuum Circuit Breaker of 630 A |  |  |
|  | Description of the Item | Vacuum Circuit Breaker |  |
|  | Certifications | To be mentioned |  |
|  | Model Number | To be mentioned |  |
|  | Rated Frequency | 50 Hz |  |
|  | Rated Nominal Voltage | 33 kV |  |
|  | Maximum Rated Voltage | 36 kV |  |
|  | Rated Nominal Current | 630 A |  |
|  | Number of Breaks Per Phase | To be mentioned |  |
|  | Interrupting Medium | Vacuum |  |
|  | Basic Insulation Level | 170 kV peak (1.2/50 µs) |  |
|  | Power Frequency Withstand Voltage | 70 kV (For 1 Minute @ 50 Hz) |  |
|  | Rated lightning impulse withstand voltage | 170 kV |  |
|  | VCB Interrupter | Class E2C2M2 or Higher |  |
| B. PROTECTION CONTROL & METERING |  |  |  |
| 8 | Transformer Relay Protection | 50/51, 50N/51N, 87T (64REF), 24, 59, 27, 67, 67N etc |  |
|  | Manufacture's Name Country of Origin | Alstom (UK)/(France)/ABB, Switzerland or Sweden/ Siemens, Germany |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of relay | Numerical programmable Multifunction |  |
|  | The Relay protocol | IEC 61850 type |  |
| 9 | Separate Auxiliary Flag Relays for Transformer self-protection (OTA, OTT, WTA, WTT, BA, BT, OLTC Surge, PRD for main tank. |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no | Shall be mentioned |  |
|  | Type of Relays | Shall be mentioned |  |
| 10 | Trip Circuit Supervision (TCS) Relay (Separate Relay for each trip coil) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of Relay | Shall be mentioned |  |
| 11 | Trip Relay (Separate Relay) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Operating Time, ms | <10 |  |
|  | Self-reset type for O/C, E/F protection | Yes |  |
|  | Hand & Electrical reset type for Differential, REF and Transformer Self-protection | Yes |  |
| 12 | Annunciator |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Windows, nos. | 24 |  |
|  | Built in buzzer and buttons for accept, mute, test, reset, etc. | Yes |  |
| 13 | Control Switch |  |  |
|  | Manufacture's Name & Country | Shall be mentioned |  |
|  | Manufacture's Model/Type No. | Shall be mentioned |  |
|  | Separate TNC/Discrepancy switch and Local Remote (L/R) selector switch | Yes |  |
| 14 | AVR Relay: Transformer incomer PCM panel shall be equipped with AVR relay and control switch for RTCC operation along with necessary indication system (Tap position, oil temperature, winding temperature etc.). | Yes |  |
| 15 | METERING AND INSTRUMENTATION |  |  |
| 15.1 | KWH & kVARH Meter |  |  |
|  | Manufacture’s Name & Country | Landis+Gyr/EDMI-MK6E/ELSTER or approved equivalent |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Numerical programmable Multifunction |  |
|  | Class of Accuracy | 0.2 |  |
| 15.2 | VOLT METERS with Selector Switch |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 90 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
| 15.3 | AMPERE METERS |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 240 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
|  | Separate A-meter for each phase | Yes |  |
|  | Mega Watt (MW) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 15.4 | Mega VAR (MVAR) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 16 | The PCM Panel Shall be complied all the technical specification mentioned Voll-2 | Yes |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.5 Switchgear, Control & Protection Panel (1250A)-Outgoing/Grid

| Sl No | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| 1. | Description of the Item | MV Switchgear and Metering Panel |  |
| 2. | Standard | Relevant ANSI / IEC Standard |  |
| 3. | System nominal voltage kV | 33 |  |
| 4. | Maximum System Voltage, kV | 36 |  |
| 5. | Rated Frequency Hz | 50 |  |
| A | Vacuum Circuit Breaker of 1250 A |  |  |
|  | Description of the Item | Vacuum Circuit Breaker |  |
|  | Certifications | To be mentioned |  |
|  | Model Number | To be mentioned |  |
|  | Rated Frequency | 50 Hz |  |
|  | Rated Nominal Voltage | 33 kV |  |
|  | Maximum Rated Voltage | 36 kV |  |
|  | Rated Nominal Current | 1250 A |  |
|  | Number of Breaks Per Phase | To be mentioned |  |
|  | Interrupting Medium | Vacuum |  |
|  | Basic Insulation Level | 170 kV peak (1.2/50 µs) |  |
|  | Power Frequency Withstand Voltage | 70 kV (For 1 Minute @ 50 Hz) |  |
|  | Rated lightning impulse withstand voltage | 170 kV |  |
|  | VCB Interrupter | Class E2C2M2 or Higher |  |
| B. PROTECTION CONTROL & METERING |  |  |  |
| 8 | Line Protection Relay | 50/51, 50N/51N, 87L, 27, 59, 59N, 67, 67N, 50BF etc |  |
|  | Manufacture's Name Country of Origin | Alstom (UK)/(France)/ABB, Switzerland or Sweden/ Siemens, Germany |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of relay | Numerical programmable Multifunction |  |
|  | The Relay protocol | IEC 61850 type |  |
| 10 | Trip Circuit Supervision (TCS) Relay (Separate Relay for each trip coil) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Type of Relay | Shall be mentioned |  |
| 11 | Trip Relay (Separate Relay) |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Operating Time, ms | <10 |  |
|  | Self-reset type for O/C, E/F protection | Yes |  |
|  | Hand & Electrical reset type for Differential, REF and Transformer Self-protection | Yes |  |
| 12 | Annunciator |  |  |
|  | Manufacture's Name | Shall be mentioned |  |
|  | Country of Origin | Shall be mentioned |  |
|  | Manufacture's Model no. | Shall be mentioned |  |
|  | Windows, nos. | 24 |  |
|  | Built in buzzer and buttons for accept, mute, test, reset, etc. | Yes |  |
| 13 | Control Switch |  |  |
|  | Manufacture's Name & Country | Shall be mentioned |  |
|  | Manufacture's Model/Type No. | Shall be mentioned |  |
|  | Separate TNC/Discrepancy switch and Local Remote (L/R) selector switch | Yes |  |
| 14 | METERING AND INSTRUMENTATION |  |  |
| 14.1 | KWH & kVARH Meter |  |  |
|  | Manufacture’s Name & Country | Landis+Gyr/EDMI-MK6E/ELSTER or approved equivalent |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Numerical programmable Multifunction |  |
|  | Class of Accuracy | 0.2 |  |
| 14.2 | VOLT METERS with Selector Switch |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 90 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
| 14.3 | AMPERE METERS |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, 240 degree scale range |  |
|  | Class of Accuracy | 1.0 |  |
|  | Separate A-meter for each phase | Yes |  |
|  | Mega Watt (MW) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 14.4 | Mega VAR (MVAR) Meter |  |  |
|  | Manufacturer’s Name and Country | Shall be mentioned |  |
|  | Manufacture’s Model no. | Shall be mentioned |  |
|  | Type of Meter | Analogue, Import/Export |  |
|  | Class of Accuracy | 1.0 |  |
| 15 | The PCM Panel Shall be complied all the technical specification mentioned Vol-2 (Part A) | Yes |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.6:  Battery Charger

| SL No. | Description | Minimum Requirements |  | Guaranteed |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
|  | Manufacturer |  |  |  |
|  | Type designation |  |  |  |
|  | Type |  | Thyristor controlled |  |
|  | Country of origin |  | - |  |
|  | Standards |  | IEC |  |
|  | Rated input voltage | V | 3 x 400 / 230 |  |
|  | Rated input current (at rated output) | A | To be mentioned |  |
|  | Input voltage variation | % | ±5 |  |
|  | Power factor | 1 | > 0,80 |  |
|  | Efficiency | % | > 85 |  |
|  | Degree of protection |  | IP42 |  |
|  | Noise level | dB | < 65 dB max |  |
|  | Type of rectifiers |  | Modular with MCU |  |
|  | Number of modules (n+2) | pcs | To be mentioned |  |
|  | Module rated output current | A | To be mentioned |  |
|  | MCU protocol |  | IEC 61850 |  |
|  | Charging characteristic |  | Both constant current & constant voltage |  |
|  | Rated frequency | Hz | 50 |  |
|  | Insulation - HV, between input and output/ground | V AC, min | 1000 V AC, 1 min |  |
|  | Insulation resistance | MW; V DC, min | 10 MW, 500 V DC, 1 min |  |
|  | Rated capacity | kVA | To be mentioned |  |
|  | Rated output voltage | V d.c. | To be mentioned |  |
|  | Rated output current | A | 100 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Voltage & Frequency variation | % | ±5 |  |
|  | Voltage ripple | % | ±5 |  |
|  | Ripple frequency | Hz | ±2 |  |
|  | Charge modes | - | 3 levels: charge, float & boost |  |
|  | Float voltage per cell | V | 1.42 |  |
|  | Boost voltage per cell | V | 1.53 |  |
|  | Float & Boost voltage adjustable | - | Yes |  |
|  | Measurement |  | Input voltage Output voltage Output current Battery current Load current Earth-fault voltage |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.7: UPS and Battery

| Sl. No. | Item | To be Proposed by the Bidder |
| --- | --- | --- |
|  | Manufacturer |  |
|  | Country of Manufacture |  |
|  | Model |  |
|  | Voltage output (V) |  |
|  | Regulation (± %) |  |
|  | Frequency (Hz) |  |
|  | Power Rating (VA) |  |
|  | Load Power Factor |  |
|  | Load Crest Factor |  |
|  | Transfer Time (ms) |  |
|  | Current (A) |  |
|  | Overload Capability (%) |  |
|  | Waveform |  |
|  | Distortion (< %) |  |
|  | Transient Regulation (± 5%) |  |
| UPS Input |  |  |
|  | Voltage (V) |  |
|  | Voltage Range (+% -%) |  |
|  | Frequency (Hz) |  |
|  | Maximum Current (A) |  |
|  | Power Factor |  |
| UPS Battery |  |  |
|  | Type |  |
|  | Rating (V – Ah) |  |
|  | Number of Cells |  |
|  | Autonomy Time at full load (min) |  |
|  | Recharge Time to 90% capacity as multiple of outage time |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.8: Pyranometer

| SL No | Description | Purchaser's Requirement | Manufacturer’s Particulars |
| --- | --- | --- | --- |
| Pyranometer |  |  |  |
| 01 | Description of the Item | Pyranometer |  |
| 02 | Name of the Manufacturer | To be mentioned |  |
| 03 | Standard | Design, manufacturing, performance & testing shall be in accordance to the IEC or equivalent international standards. |  |
| 04 | Model number | To be mentioned |  |
| 05 | Spectral Range | 285 to 2800 nm |  |
| 06 | Sensitivity | 7 to14 µV/W/m2 |  |
| 07 | Response Time | < 5 s |  |
| 08 | Zero Offset A | < 7 W/ m2 |  |
| 09 | Zero Offset B | < 2 W/ m2 |  |
| 10 | Direction Error (up to 80º with 1 Sun irradiance) | < 10 W/ m2 |  |
| 11 | Operating Temperature Range | -40º C to +80º C |  |
| 12 | Temperature Dependence of Sensitivity (-40º C to +80º C ) | < 1% |  |
| 13 | Maximum Solar Irradiance | 4000 W/ m2 |  |
| 14 | Field of View | 180 º |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.9 SCADA Server

| No. | Description | Minimum Requirements |  | Guaranteed |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
|  | SCADA Server |  |  |  |
| 1.1 | Manufacturer |  | Insert |  |
| 1.2 | Country of origin |  | Insert |  |
| 1.3 | Type |  | Insert |  |
| 1.4 | Standards |  | IEC |  |
| 1.5 | Type of housing |  | Industrial 19" rack |  |
| 1.6 | SCADA server | Pcs | 2 |  |
| 1.7 | Ethernet switch-process LAN | pcs. | 2 |  |
| 1.8 | Ethernet switch-control room LAN | pcs. | 2 |  |
| 2. | Characteristics |  |  |  |
| 2.1 | Auxiliary supply voltage |  |  |  |
| 2.1.1 | Rated auxiliary supply voltage | V d.c. | 110 ±15 % |  |
| 2.1.2 | Dual power supply |  | Yes |  |
| 2.2 | Processor type |  | Insert |  |
| 2.3 | Processor clock | GHz | Insert |  |
| 2.4 | Memory type |  | Insert |  |
| 2.5 | Memory capacity | MB | Insert |  |
| 2.6 | Video display adapter type |  | Insert |  |
| 2.7 | Video display adapter memory |  | Insert |  |
| 2.8 | Hard disc type |  | Insert |  |
| 2.9 | Rotating hard disc | Yes/No | Insert |  |
| 2.10 | Hard disc capacity | GB | Insert |  |
| 2.11 | Number of hard discs | pcs. | Insert |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.10. SCADA Software

| No. | Description | Minimum Requirements |  | Guaranteed |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
| 1.1 | Basic SCADA server software |  |  |  |
| 1.1 | Basic SCADA server software | pcs. | 2 |  |
| 1.1.1 | Communication with 2 higher level control centers |  | Yes |  |
| 1.1.2 | Real-time database management |  | Yes |  |
| 1.1.3 | Data processing |  | Yes |  |
| 1.1.4 | Data acquisition |  | Yes |  |
| 1.1.5 | Alarm and event processing |  | Yes |  |
| 1.1.6 | Data archiving |  | Yes |  |
| 1.1.7 | Report generation and printing |  | Yes |  |
| 1.1.8 | Redundancy management |  | Yes |  |
| 1.2 | Operator workstation software | pcs. | 2 |  |
| 1.3 | Communication software | pcs. | 2 |  |
| 1.3.1 | Communication with 2 higher level control centers |  | Yes |  |
| 1.4 | Application libraries | pcs. | 1, optional |  |
| 1.5 | Software tools | pcs. | 1 |  |
| 1.5.1 | Database creating, maintaining and viewing |  | Yes |  |
| 1.5.2 | User interface definition |  | Yes |  |
| 1.5.3 | Report definition |  | Yes |  |
| 1.5.4 | System configuration |  | Yes |  |
| 1.5.5 | Historical data maintaining |  | Yes |  |
| 1.5.6 | Database and historical data export/import |  | Yes |  |
| 1.5.7 | Analysis and diagnostic tools |  | Yes |  |
| 1.5.8 | Training simulator |  | Yes |  |
| 1.5.9 | Other software tools according to Contractor's concept: |  | Insert |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.11. Energy Meter

| Sl. No. | Description |  | Required Specification | Manufacture’s particulars |
| --- | --- | --- | --- | --- |
| 1 | Reference Standard |  | Relevant ANSI / IEC Standard |  |
| 2 | Manufacturer’s name & address |  | Shall be mentioned |  |
| 3 | Manufacturer’s type & model |  | Shall be mentioned |  |
| 4 | Construction/connection |  | 3-Phase 4-wire solidly grounded neutral |  |
| 5 | Installation |  | Indoor installation in A socket [for socket type] |  |
| 6 | Number of elements |  | 3 (Three) |  |
| 7 | Rated Voltage, Volt |  | 110V |  |
| 8 | Minimum Biasing Voltage, Volt |  | 40V |  |
| 9 | Variation of Frequency, % |  | ± 2.5% |  |
| 10 | Variation of Voltage, % |  | -20% to + 10% |  |
| 11 | Accuracy class |  | 0.2 (point two) S |  |
| 12 | Rated Current |  |  |  |
|  | i) | Nominal Current, A | = 5 |  |
|  | ii) | Maximum Current, A | > 6 |  |
| 13 | Resister Type |  | LCD Display |  |
| 14 | Number of Digits (Integer with Decimal), Nos. |  | 5 with 3 (Programmable) |  |
| 15 | Starting Current, ma |  | 0.1% of Nominal Current |  |
| 16 | Losses at Nominal Load, Watt |  | Shall be mentioned |  |
| 17 | Meter Constant, Imp./ |  | Shall be mentioned |  |
| 18 | Integration Period |  | 30 (Thirty) Minutes |  |
|  | Resetting Period |  | 1 (one) month |  |
|  | Cumulative MD transfer |  | Built in |  |
|  | Cycle Timing Device |  | Built in |  |
| 19 | Size of the Digit of Display, E x H in mm |  | 4 x 8 |  |
| 20 | No. of Terminal, Nos. |  | 10 (Ten) min |  |
| 21 | Type of socket and country of origin |  | To be mentioned |  |
| 22 | Battery Service life and shelf Life (minimum), Year |  | 10 (ten) & 15 (fifteen) |  |
| 23 | Year of manufacture |  | Shall be mentioned |  |
| 24 | List of Recommended spare parts (if any) , any |  | Shall be mentioned |  |
| 25 | Warranty, Year |  | 2 (two) |  |
| 26 | Meter Service Life (Min), Year |  | 15 (fifteen) |  |
| 27 | Weight of meter, Kg |  | Shall be mentioned |  |
| 28 | Dimensions , mm x mm x mm |  | Shall be mentioned |  |
| 29 | Outlines, Drawings & Leaflets |  | Shall be mentioned |  |
| 30 | Performance Curve for Balanced & Unbalanced load |  | Shall be mentioned |  |
| 31 | Meter sealing condition |  | Hermetically or Ultrasonic welded (Break to open) |  |
| 32 | Meter parameter configuration |  | To be configured (Both software and hardware lock) |  |
| 33 | Losses of nominal Load, Watt &VA |  | To be mentioned |  |
| 34 | Current circuit loss at rated current, VA |  | To be mentioned |  |
| 35 | Application protocol |  | DLMS/COSEM |  |
| 36 | Communication (if required) |  | Plug & play 4G communication module |  |
| 37 | a) Country of Origin b) Place of Manufacture c) Place of Testing |  | Shall be mentioned |  |
| 38 | Memory Storage |  | Shall be mentioned by putting Yes/ No. |  |
|  | i) | Equipment Identification Code |  |  |
|  | ii) | Security code |  |  |
|  | iii) | Access code |  |  |
|  | iv) | Number of Power Interruption with Date & Time |  |  |
|  | V | Latest Power Failure- Time & Date |  |  |
|  | Vi | Event logs |  |  |
|  | vii) | Cumulative kWh, kVarh (Q1 + Q4) Reading for previous two months |  |  |
|  | viii) Load profile with 30 min interval at least 90 days for: |  |  |  |
|  |  | KWh, kVarh (Q1+Q4) |  |  |
|  |  | Phase Voltage or Vh |  |  |
|  |  | Phase Amps or Ah |  |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.12 Auxiliary Transformer

| No. | Description | Minimum Requirements |  | Manufacture’s particulars |
| --- | --- | --- | --- | --- |
|  |  | Unit | Data |  |
| 1. | General |  |  |  |
| 1.1 | Manufacturer |  | To be mentioned |  |
| 1.2 | Type Type |  | Auxiliary station transformer |  |
| 1.3 | Model |  | To be mentioned |  |
| 1.4 | Country of origin |  | To be mentioned |  |
| 1.5 | Standards |  | IEC 60076 |  |
| 2. | Ratings and properties |  |  |  |
| 2.1 | Rated power | kVA | 250 |  |
| 2.2 | Type of cooling | - | ONAN |  |
| 2.3 | Rated voltage | kV/V | 33 ± 2 x 2,5 % / 415 |  |
| 2.4 2.4 | Tap changer (off-circuit tap changer) |  | ±2 × 2.5% |  |
| 2.5 | Frequency | Hz | 50 |  |
| 2.6 | Vector Group |  | Dyn11 |  |
| 3. | Special technical requirements |  |  |  |
| 3.1 | No-load losses | kW | To be mentioned |  |
| 3.2 | On-load losses | kW | To be mentioned |  |
| 3.3 | Insulation-Medium voltage (MV) |  | LI 170 AC 70 |  |
| 3.4 | Insulation-Low voltage (LV) |  | LI - AC 3 |  |
| 3.5 | Highest System Voltage (MV) Side | kV | 36 |  |
| 3.6 | Highest System Voltage (LV) Side | kV | 1.1 |  |
| 4. | Oil |  |  |  |
| 4.1 | Standard |  | IEC 60296 |  |
| 4.2 | Minimum flash point | °C | To be mentioned |  |
| 4.3 | Viscosity at 20°C | mm2/s | To be mentioned |  |
| 4.4 | Minimum dielectric strength | kV/cm | To be mentioned |  |
| 5. | Bushing |  |  |  |
| 5.1 | MV bushing (36 kV) |  |  |  |
| 5.1.1 | Quantity |  | 3 + 1 |  |
| 5.1.2 | Class | kV | 36/170/70 |  |
| 5.1.3 | Minimum creepage distance (25 mm/ kV) | mm/ kV | ≥ 25 mm/ kV |  |
| 5.2 | LV bushings (3 kV) |  |  |  |
| 5.2.1 | Quantity |  | 3 + 1 |  |
| 5.2.2 | Class | kV | 3 |  |
| 5.2.3 | Minimum creepage distance (25 mm/ kV) | mm/ kV | ≥ 25 mm/ kV |  |
| 6. | Dehydrating breather |  |  |  |
| 6.1 | Type of dehydrating breather |  | To be mentioned |  |
| 6.2 | Dehumidifying agent | kg | To be mentioned |  |
| 7 | Conservator |  |  |  |
| 7.1 | Type |  | With dehydrating breather |  |
| 7.2 | Number of compartments | pcs. | 1 |  |
| 7.3 | Oil level indicators with alarm for minimum oil level | pcs. | 1 |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.13 Current Transformer

| Sl. No. | Description | Unit | BPDB's Requirement | Manufacture’s particulars |
| --- | --- | --- | --- | --- |
| 1. | Manufacturer’s Name & country of origin | - | To be mentioned |  |
| 2. | Manufacturer’s Model no. | - | To be mentioned |  |
| 3. | Application |  | Metering and Protection |  |
| 4. | Installation | - | Indoor |  |
| 5. | CT Ratio |  |  |  |
|  | (a) Transformer Protection | A | 200-400/1-1 A |  |
|  | (b) Evacuation | A | 400-800/1-1-1 A |  |
| 6. | Accuracy Class |  |  |  |
|  | a) For Measurement | - | 0.2S |  |
|  | b) For Measurement | - | 5P20 |  |
| 7. | Burden |  |  |  |
|  | a) For Measurement (at half ratio) (minimum) | VA | 10 VA |  |
|  | b) For Measurement (at full ratio) (minimum) | VA | 20 VA |  |
| 8. | Instrument Security factor (Measuring Core) |  | To be mentioned |  |
| 9. | Rated Accuracy Limit factor (ALF) | - | 20 (Minimum) |  |
| 10. | RCT at 75⁰C (Half Tap- Full Tap): |  |  |  |
|  | a) For Measurement Core: To be Mentioned |  | To be mentioned |  |
|  | b) For Protection Core: To be Mentioned |  | To be mentioned |  |
| 11. | Knee-point Minimum Voltage (Supported by Calculation) |  |  |  |
|  | (a) Measuring Core | V | To be mentioned |  |
|  | (b) Protection Core | V | To be mentioned |  |
| 12. | Short Time Current Rating for 3 sec | kA | 40 |  |
| 13. | Standard (Design, Manufacture, Testing, Installation and Performance) | - | Latest editions of the relevant IEC 61869-1 and IEC 61869-2 |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |

2.13 Potential Transformer

| Sl. No. | Description | Unit | BPDB's Requirement | Manufacture’s particulars |
| --- | --- | --- | --- | --- |
| 1. | Manufacturer’s Name & country of origin | - | To be mentioned |  |
| 2. | Manufacturer’s Model no. | - | To be mentioned |  |
| 3. | Application |  | Metering and Protection |  |
| 4. | Installation | - | Indoor |  |
| 5. | PT Ratio (with one core open delta) | kV | (33/3)/ (0.11/3) / (0.11/3)/0.11/3 |  |
| 6. | Accuracy Class |  |  |  |
|  | a) For Measurement | - | 0.2 |  |
|  | b) For Protection | - | 3P |  |
| 7. | Burden |  |  |  |
|  | a) For Measurement (at half ratio) (minimum) | VA | 10 VA |  |
|  | b) For Protection (at half ratio) (minimum) | VA | 20 VA |  |
| 8. | Instrument Security factor (Metering Core) |  | To be mentioned |  |
| 9. | Rated Accuracy Limit factor (ALF) |  |  |  |
|  | (a) Protection Core @ half tap | - | To be mentioned |  |
|  | (a) Protection Core @ full tap | - | To be mentioned |  |
| 11. | Standard (Design, Manufacture, Testing, Installation and Performance) | - | Latest editions of the relevant IEC 61869-1 and IEC 61869-2 |  |

| Seal & Signature of the Manufacturer | Seal & Signature of the Bidder |
| --- | --- |